{"text_format":"2","workbook":"xlsx","n_sheets":7,"sheets":["BA+(間引き+仮想DI)","传感器列表","butics-ax设备","抄表项目","人员定位","数据点","Sheet1"],"not_rendered":{"charts":0,"images":2,"macros":0,"external_links":0,"defined_names":3,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"BA+(間引き+仮想DI)","index":0,"n_rows":324,"n_cols":41,"rows_kept":324,"cut":false,"hidden":false,"merged":[[236,26,237,26],[238,26,240,26],[253,26,254,26],[258,26,259,26],[273,26,280,26],[281,26,288,26],[289,26,290,26],[294,26,295,26],[298,26,301,26],[236,27,237,27],[238,27,240,27],[253,27,254,27],[258,27,259,27],[273,27,280,27],[281,27,288,27],[289,27,290,27],[294,27,295,27],[298,27,301,27]]}
[]
[null,null,"■点検ルート",null,"設備点検","検針","■ZETAセンサ","■ＢＡ仮想ﾎﾟｲﾝﾄ","■ビーコン（バイタル）",null,"データ取り込みのコンセプト",{"$nulls":19},"検針","■ＢＡ仮想ﾎﾟｲﾝﾄ","■ビーコン（バイタル）"]
[null,null,"オフィス棟１Ｆ",null,"○","○","オフィス棟１Ｆ","オフィス棟１Ｆ","オフィス棟１Ｆ",null,"・点検ルート上の設備点検・検針はトラッカーで実施する",{"$nulls":19},"○","オフィス棟１Ｆ","オフィス棟１Ｆ"]
[null,null,"オフィス棟７Ｆ",null,"○",null,"オフィス棟７Ｆ","オフィス棟７Ｆ","オフィス棟７Ｆ",null,"・検針ポイントはBA仮想ポイントも作成する（DBMには2重で定義される）",{"$nulls":20},"オフィス棟７Ｆ","オフィス棟７Ｆ"]
[null,null,"オフィス棟ＲＦ",null,"○","○",null,null,"オフィス棟ＲＦ",{"$nulls":21},"○",null,"オフィス棟ＲＦ"]
[{"$nulls":6},"実験棟４Ｆ","実験棟４Ｆ","実験棟４Ｆ",{"$nulls":22},"実験棟４Ｆ","実験棟４Ｆ"]
[null,null,"実験棟６ＲＦ",null,"○","○","実験棟６ＲＦ","実験棟６ＲＦ","実験棟６ＲＦ",{"$nulls":21},"○","実験棟６ＲＦ","実験棟６ＲＦ"]
[{"$nulls":6},"鉄塔地上",null,null,null,"Seer（アカウント20、空間分割20）"]
[{"$nulls":6},"鉄塔上部",null,null,null,"Sentry(アカウント20、ポイント100)"]
[{"$nulls":6},"倉庫1F",null,null,null,"Tracker(アカウント20、ポイント10)"]
[]
[null,"点検時刻",null,"場所",null,"設備名称","分類","機器名称","点検項目","データ","単位","全点検","簡易点検","写真","BA仮想","ZETA","Tracker","Sentry","NFC","空間","経路","正常:0","異常:1","Tracker記載内容","最大値","最小値","型番","ＩＤ","指標ID",null,"DBM設備分類","DBM設備名称","DBM点検項目",{"$nulls":5},"デバイスID","センサー種別","GodziraID"]
[null,null,"ｵﾌｨｽ棟","１Ｆ","警備室","自火報設備","設備点検","交流電源","ランプ表示",null,"点燈／消燈","○","×","○",null,null,"○",null,"①","①","A","点燈","消燈","自火報設備の交流電源のランプ表示点燈していること",null,null,"ー","ー","ー",null,"自火報設備","自火報設備　交流電源","ランプ表示"]
[{"$nulls":6},"設備点検",null,"回路電圧",null,"点燈／消燈","○","×","○",null,null,"○",null,"①","①","A","点燈","消燈","自火報設備の交流電源の回路電圧が点燈していること",null,null,"ー","ー","ー",null,null,null,"回路電圧"]
[null,null,"ｵﾌｨｽ棟","１Ｆ","消火ポンプ室","消火栓ポンプ","設備点検",null,"入口扉施錠　",null,"有／無","○","×","○",null,null,"○",null,"②","②","A","施錠","開錠","消火栓ポンプの入口扉が施錠されていること",null,null,"ー","ー","ー",null,"消火栓ポンプ","消火栓ポンプ","入口扉施錠　"]
[{"$nulls":6},"設備点検",null,"異音",null,"有／無","○","×",null,null,null,"○",null,"②","②","A","無","有","消火栓ポンプに異音が無いこと",null,null,"ー","ー","ー",null,null,null,"異音"]
[{"$nulls":6},"設備点検",null,"異臭",null,"有／無","○","×",null,null,null,"○",null,"②","②","A","無","有","消火栓ポンプに異臭が無いこと",null,null,"ー","ー","ー",null,null,null,"異臭"]
[{"$nulls":6},"設備点検",null,"水漏れ",null,"有／無","○","×","○",null,null,"○",null,"②","②","A","無","有","消火栓ポンプに水漏れが無いこと",null,null,"ー","ー","ー",null,null,null,"水漏れ"]
[{"$nulls":6},"設備点検",null,"表示灯",null,"点燈／消燈","○","×","○",null,null,"○",null,"②","②","A","点燈","消燈","消火栓ポンプの表示灯が点燈していること",null,null,"ー","ー","ー",null,null,null,"表示灯"]
[{"$nulls":6},"検針",null,"表示電圧",null,"V","○","×","○",null,null,"○",null,"②","②","Ｂ",null,null,"消火栓ポンプの表示電圧「〇〇」Ｖ",null,null,"ー","ー",null,null,"消火栓ポンプ","消火栓ポンプ　表示灯","表示電圧"]
[{"$nulls":6},"検針",null,"表示電圧(B)",null,"V",null,null,null,"○",null,null,"○","②","②","Ｅ",{"$nulls":5},"ー","60e8fd7b-501e-372b-9fc0-e1de27d51d35-AI",null,null,null,"消火栓ポンプ　表示灯(B)","表示電圧(B)"]
[null,null,"ｵﾌｨｽ棟","１Ｆ","消火ポンプ室","泡消火栓ポンプ","設備点検",null,"異音",null,"有／無","○","×",null,null,null,"○",null,"②","②","A","無","有","泡消火栓ポンプに異音が無いこと",null,null,"ー","ー","ー",null,"泡消火栓ポンプ","泡消火栓ポンプ","異音"]
[{"$nulls":6},"設備点検",null,"異臭",null,"有／無","○","×",null,null,null,"○",null,"②","②","A","無","有","泡消火栓ポンプに異臭が無いこと",null,null,"ー","ー","ー",null,null,null,"異臭"]
[{"$nulls":6},"設備点検",null,"水漏れ",null,"有／無","○","×",null,null,null,"○",null,"②","②","A","無","有","泡消火栓ポンプに水漏れが無いこと",null,null,"ー","ー","ー",null,null,null,"水漏れ"]
[{"$nulls":6},"検針","タンク","圧力",null,"Mpa","○","×",null,null,null,"○",null,"②","②","Ｂ",null,null,"泡消火栓ポンプのタンク圧力「〇〇」Mpa",null,null,"ー","ー",null,null,null,"泡消火栓ポンプ　タンク","圧力"]
[{"$nulls":6},"検針","タンク","圧力(B)",null,"Mpa",null,null,null,"○",null,null,"○","②","②","Ｅ",{"$nulls":5},"ー","7cceca42-fa6d-3783-9968-fb691e5d3cec-AI",null,null,null,"泡消火栓ポンプ　タンク(B)","圧力(B)"]
[null,null,"ｵﾌｨｽ棟","１Ｆ","入口","加圧給水ポンプ","設備点検",null,"異音",null,"有／無",null,null,null,"○",null,null,"○","×","③","Ｅ","無","有",null,null,null,"ー","c4125810-9483-37be-9fe7-8564845fab39-BI",null,null,"加圧給水ポンプ","加圧給水ポンプ(B)","異音(B)"]
[{"$nulls":6},"設備点検",null,"異臭",null,"有／無",null,null,null,"○",null,null,"○","×","③","Ｅ","無","有",null,null,null,"ー","fdfc2ab0-3e32-31c4-8c50-593b405a47bb-BI",{"$nulls":4},"異臭(B)"]
[{"$nulls":6},"設備点検",null,"水漏れ",null,"有／無",null,null,null,"○",null,null,"○","×","③","Ｅ","無","有",null,null,null,"ー","223132d1-9b22-36b5-9987-bb88e8d6b7d5-BI",{"$nulls":4},"水漏れ"]
[{"$nulls":6},"設備点検",null,"施錠",null,"有／無",null,null,null,"○",null,null,"○","×","③","Ｅ","施錠","開錠",null,null,null,"ー","8ffca40a-0a99-3ef7-9962-03d8ba12a924-BI",{"$nulls":4},"施錠"]
[{"$nulls":6},"設備点検",null,"制御電源表示灯",null,"点燈／消燈",null,null,null,"○",null,null,"○","×","③","Ｅ","点灯","消灯",null,null,null,"ー","b727daff-7cc1-3fa4-81a3-726bb9e09baa-BI",{"$nulls":4},"制御電源表示灯"]
[{"$nulls":6},"検針",null,"設定揚程(24-68m)",null,"ｍ","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"設定揚程(24-68m)"]
[{"$nulls":6},"検針",null,"設定揚程(24-68m)",null,"ｍ","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"設定揚程(24-68m)"]
[{"$nulls":6},"検針","動作ポンプ","動作ポンプ№(1,2,3)",null,"－","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,"動作ポンプ","動作ポンプ№(1,2,3)"]
[{"$nulls":6},"検針","動作ポンプ","動作ポンプ№(1,2,3)",null,"－","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,"動作ポンプ","動作ポンプ№(1,2,3)"]
[{"$nulls":5},"水道メイン","検針",null,"当日メータ値",null,"m3","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,"水道メイン",null,"当日メータ値"]
[{"$nulls":6},"検針",null,"当日メータ値",null,"m3","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"当日メータ値"]
[null,null,"ｵﾌｨｽ棟","１Ｆ","EPS","雨水ポンプ","設備点検","マンホール","蓋",null,"有／無","○","×","○",null,null,"○",null,"④","④","A","閉","開","雨水ポンプのマンホールの蓋が閉まっていること",null,null,"ー","ー","ー",null,"雨水ポンプ","雨水ポンプ　マンホール","蓋"]
[{"$nulls":6},"設備点検","制御盤","スイッチ位置",null,"自動／自交","○","×","○",null,null,"○",null,"④","④","A","自動","自交","雨水ポンプの制御盤のスイッチ位置が自動であること",null,null,"ー","ー","ー",null,null,"雨水ポンプ　制御盤","スイッチ位置"]
[{"$nulls":6},"検針","制御盤№１","電流",null,"A","○","×","○",null,null,"○",null,"④","④","Ｂ",null,null,"雨水ポンプの制御盤No.1の電流「〇〇」A",null,null,"ー","ー",null,null,null,"雨水ポンプ　制御盤№１","電流"]
[{"$nulls":6},"検針","制御盤№１","電流(B)",null,"A",null,null,null,"○",null,null,"○","④","④","Ｅ",{"$nulls":5},"ー","6f8aef15-b6cb-32aa-8c94-4cfce134a9cf-AI",null,null,null,"雨水ポンプ　制御盤№１(B)","電流(B)"]
[{"$nulls":6},"検針","制御盤№２","電流",null,"A","○","×","○",null,null,"○",null,"④","④","Ｂ",null,null,"雨水ポンプの制御盤No.2の電流「〇〇」A",null,null,"ー","ー",null,null,null,"雨水ポンプ　制御盤№２","電流"]
[{"$nulls":6},"検針","制御盤№２","電流(B)",null,"A",null,null,null,"○",null,null,"○","④","④","Ｅ",{"$nulls":5},"ー","379adc2b-f648-3e72-8a58-c77d69e598d5-AI",null,null,null,"雨水ポンプ　制御盤№２(B)","電流(B)"]
[null,null,"ｵﾌｨｽ棟","１Ｆ",null,"自動ドア","設備点検",null,"扉開閉",null,"正常／異常","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,"自動ドア",null,"扉開閉"]
[{"$nulls":8},"センサー反応",null,"正常／異常","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"センサー反応"]
[null,null,"ｵﾌｨｽ棟","１Ｆ",null,"エレベータ","設備点検","乗り場","扉開閉",null,"正常／異常","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,"エレベータ","乗り場","扉開閉"]
[{"$nulls":8},"ボタン損傷",null,"有／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"ボタン損傷"]
[{"$nulls":8},"かごと床の段差",null,"有／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"かごと床の段差"]
[{"$nulls":7},"かご","異音",null,"有／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,"かご","異音"]
[{"$nulls":8},"振動",null,"有／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"振動"]
[null,null,"ｵﾌｨｽ棟","２Ｆ",null,"エレベータ","設備点検","乗り場","扉開閉",null,"正常／異常","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,"エレベータ","乗り場","扉開閉"]
[{"$nulls":6},"設備点検",null,"ボタン損傷",null,"有／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"ボタン損傷"]
[{"$nulls":6},"設備点検",null,"かごと床の段差",null,"有／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"かごと床の段差"]
[{"$nulls":6},"設備点検","かご","異音",null,"有／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,"かご","異音"]
[{"$nulls":6},"設備点検",null,"振動",null,"有／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"振動"]
[null,null,"ｵﾌｨｽ棟","３Ｆ",null,"エレベータ","設備点検","乗り場","扉開閉",null,"正常／異常","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,"エレベータ","乗り場","扉開閉"]
[{"$nulls":6},"設備点検",null,"ボタン損傷",null,"有／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"ボタン損傷"]
[{"$nulls":6},"設備点検",null,"かごと床の段差",null,"有／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"かごと床の段差"]
[{"$nulls":6},"設備点検","かご","異音",null,"有／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,"かご","異音"]
[{"$nulls":6},"設備点検",null,"振動",null,"有／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"振動"]
[null,null,"ｵﾌｨｽ棟","３Ｆ",null,"給茶機","設備点検","充填","水",null,"補充／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,"給茶機","充填","水"]
[{"$nulls":6},"設備点検",null,"コップ",null,"補充／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"コップ"]
[{"$nulls":6},"設備点検",null,"茶",null,"補充／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"茶"]
[null,null,"ｵﾌｨｽ棟","４Ｆ",null,"エレベータ","設備点検","乗り場","扉開閉",null,"正常／異常","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,"エレベータ","乗り場","扉開閉"]
[{"$nulls":6},"設備点検",null,"ボタン損傷",null,"有／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"ボタン損傷"]
[{"$nulls":6},"設備点検",null,"かごと床の段差",null,"有／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"かごと床の段差"]
[{"$nulls":6},"設備点検","かご","異音",null,"有／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,"かご","異音"]
[{"$nulls":6},"設備点検",null,"振動",null,"有／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"振動"]
[null,null,"ｵﾌｨｽ棟","４Ｆ",null,"給茶機","設備点検","充填","水",null,"補充／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,"給茶機","充填","水"]
[{"$nulls":6},"設備点検",null,"コップ",null,"補充／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"コップ"]
[{"$nulls":6},"設備点検",null,"茶",null,"補充／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"茶"]
[null,null,"ｵﾌｨｽ棟","５Ｆ",null,"エレベータ","設備点検","乗り場","扉開閉",null,"正常／異常","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,"エレベータ","乗り場","扉開閉"]
[{"$nulls":6},"設備点検",null,"ボタン損傷",null,"有／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"ボタン損傷"]
[{"$nulls":6},"設備点検",null,"かごと床の段差",null,"有／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"かごと床の段差"]
[{"$nulls":6},"設備点検","かご","異音",null,"有／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,"かご","異音"]
[{"$nulls":6},"設備点検",null,"振動",null,"有／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"振動"]
[null,null,"ｵﾌｨｽ棟","５Ｆ",null,"給茶機","設備点検","充填","水",null,"補充／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,"給茶機","充填","水"]
[{"$nulls":6},"設備点検",null,"コップ",null,"補充／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"コップ"]
[{"$nulls":6},"設備点検",null,"茶",null,"補充／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"茶"]
[null,null,"ｵﾌｨｽ棟","６Ｆ",null,"エレベータ","設備点検","乗り場","扉開閉",null,"正常／異常","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,"エレベータ","乗り場","扉開閉"]
[{"$nulls":6},"設備点検",null,"ボタン損傷",null,"有／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"ボタン損傷"]
[{"$nulls":6},"設備点検",null,"かごと床の段差",null,"有／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"かごと床の段差"]
[{"$nulls":6},"設備点検","かご","異音",null,"有／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,"かご","異音"]
[{"$nulls":6},"設備点検",null,"振動",null,"有／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"振動"]
[null,null,"ｵﾌｨｽ棟","６Ｆ",null,"給茶機","設備点検","充填","水",null,"補充／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,"給茶機","充填","水"]
[{"$nulls":6},"設備点検",null,"コップ",null,"補充／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"コップ"]
[{"$nulls":6},"設備点検",null,"茶",null,"補充／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"茶"]
[null,null,"ｵﾌｨｽ棟","７Ｆ",null,"エレベータ","設備点検","乗り場","扉開閉",null,"正常／異常","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,"エレベータ","乗り場","扉開閉"]
[{"$nulls":8},"ボタン損傷",null,"有／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"ボタン損傷"]
[{"$nulls":8},"かごと床の段差",null,"有／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"かごと床の段差"]
[{"$nulls":7},"かご","異音",null,"有／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,"かご","異音"]
[{"$nulls":8},"振動",null,"有／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"振動"]
[null,null,"ｵﾌｨｽ棟","７Ｆ",null,"給茶機","設備点検","充填","水",null,"補充／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,"給茶機","充填","水"]
[{"$nulls":8},"コップ",null,"補充／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"コップ"]
[{"$nulls":8},"茶",null,"補充／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"茶"]
[null,null,"ｵﾌｨｽ棟","RF","屋上機器","キュービクル","検針","高圧受電盤","受電電圧",null,"V","○","×","○",null,null,"○",null,"⑤","⑤","Ｂ",null,null,"高圧受電盤の電圧「〇〇」V",null,null,"ー","ー",null,null,"キュービクル","高圧受電盤","受電電圧"]
[{"$nulls":6},"検針","高圧受電盤","受電電圧(B)",null,"V",null,null,null,"○",null,null,"○","⑤","⑤","Ｅ",{"$nulls":5},"ー","4cda80dc-571b-397c-bb41-094cd43bd7c0-AI",null,null,null,"高圧受電盤(B)","受電電圧(B)"]
[{"$nulls":6},"検針",null,"電流値",null,"A","○","×","○",null,null,"○",null,"⑤","⑤","Ｂ",null,null,"高圧受電盤の電流「〇〇」A",null,null,"ー","ー",{"$nulls":4},"電流値"]
[{"$nulls":6},"検針",null,"電流値(B)",null,"A",null,null,null,"○",null,null,"○","⑤","⑤","Ｅ",{"$nulls":5},"ー","df6ed27e-a73c-365f-b13c-361fe6b6664a-AI",{"$nulls":4},"電流値(B)"]
[{"$nulls":6},"検針",null,"電力",null,"W","○","×","○",null,null,"○",null,"⑤","⑤","Ｂ",null,null,"高圧受電盤の電圧「〇〇」W",null,null,"ー","ー",{"$nulls":4},"電力"]
[{"$nulls":6},"検針",null,"電力(B)",null,"W",null,null,null,"○",null,null,"○","⑤","⑤","Ｅ",{"$nulls":5},"ー","9933766e-3b38-32f5-ba5e-3c531f0cce36-AI",{"$nulls":4},"電力(B)"]
[{"$nulls":6},"検針","高圧引き込み盤","電力量",null,"KWH","○","×","○",null,null,"○",null,"⑤","⑤","Ｂ",null,null,"高圧引き込み盤の電力量「〇〇」KWH",null,null,"ー","ー",null,null,null,"高圧引き込み盤","電力量"]
[{"$nulls":6},"検針","高圧引き込み盤","電力量(B)",null,"KWH",null,null,null,"○",null,null,"○","⑤","⑤","Ｅ",{"$nulls":5},"ー","94a09f61-5a77-39ca-99a8-6ca64b840cce-ACC",null,null,null,"高圧引き込み盤(B)","電力量(B)"]
[{"$nulls":6},"検針","高圧饋電盤","R相",null,"A","○","×","○",null,null,"○",null,"⑤","⑤","Ｂ",null,null,"高圧饋電盤のR相電流「〇〇」A",null,null,"ー","ー",null,null,null,"高圧饋電盤","R相"]
[{"$nulls":6},"検針","高圧饋電盤","R相",null,"A",null,null,null,"×",null,null,"×","⑤","⑤","ー",{"$nulls":5},"ー","ー","ー",null,null,"高圧饋電盤","R相"]
[{"$nulls":6},"検針",null,"S相",null,"A","○","×","○",null,null,"○",null,"⑤","⑤","Ｂ",null,null,"高圧饋電盤のS相電流「〇〇」A",null,null,"ー","ー",{"$nulls":4},"S相"]
[{"$nulls":6},"検針",null,"S相",null,"A",null,null,null,"×",null,null,"×","⑤","⑤","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"S相"]
[{"$nulls":6},"検針",null,"T相",null,"A","○","×","○",null,null,"○",null,"⑤","⑤","Ｂ",null,null,"高圧饋電盤のT相電流「〇〇」A",null,null,"ー","ー",{"$nulls":4},"T相"]
[{"$nulls":6},"検針",null,"T相",null,"A",null,null,null,"×",null,null,"×","⑤","⑤","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"T相"]
[{"$nulls":6},"検針","低圧電灯配電盤No.1","電圧",null,"V","○","×",null,null,null,"○",null,"⑤","⑤","Ｂ",null,null,"低圧電灯配電盤No.1の電圧「〇〇」V",null,null,"ー","ー",null,null,null,"低圧電灯配電盤No.1","電圧"]
[{"$nulls":6},"検針","低圧電灯配電盤No.1","電圧",null,"V",null,null,null,"×",null,null,"×","⑤","⑤","ー",{"$nulls":5},"ー","ー","ー",null,null,"低圧電灯配電盤No.1","電圧"]
[{"$nulls":6},"検針",null,"電流",null,"A","○","×",null,null,null,"○",null,"⑤","⑤","Ｂ",null,null,"低圧電灯配電盤No.1の電流「〇〇」A",null,null,"ー","ー",{"$nulls":4},"電流"]
[{"$nulls":6},"検針",null,"電流",null,"A",null,null,null,"×",null,null,"×","⑤","⑤","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"電流"]
[{"$nulls":6},"検針","低圧電灯配電盤No.2","電圧",null,"V","○","×",null,null,null,"○",null,"⑤","⑤","Ｂ",null,null,"低圧電灯配電盤No.2の電圧「〇〇」V",null,null,"ー","ー",null,null,null,"低圧電灯配電盤No.2","電圧"]
[{"$nulls":6},"検針","低圧電灯配電盤No.2","電圧",null,"V",null,null,null,"×",null,null,"×","⑤","⑤","ー",{"$nulls":5},"ー","ー","ー",null,null,"低圧電灯配電盤No.2","電圧"]
[{"$nulls":6},"検針",null,"電流",null,"A","○","×",null,null,null,"○",null,"⑤","⑤","Ｂ",null,null,"低圧電灯配電盤No.2の電流「〇〇」A",null,null,"ー","ー",{"$nulls":4},"電流"]
[{"$nulls":6},"検針",null,"電流",null,"A",null,null,null,"×",null,null,"×","⑤","⑤","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"電流"]
[{"$nulls":6},"検針","低圧動力配電盤No.1","電圧",null,"V","○","×",null,null,null,"○",null,"⑤","⑤","Ｂ",null,null,"低圧動力配電盤No.1の電圧「〇〇」V",null,null,"ー","ー",null,null,null,"低圧動力配電盤No.1","電圧"]
[{"$nulls":6},"検針","低圧動力配電盤No.1","電圧",null,"V",null,null,null,"×",null,null,"×","⑤","⑤","ー",{"$nulls":5},"ー","ー","ー",null,null,"低圧動力配電盤No.1","電圧"]
[{"$nulls":6},"検針",null,"電流",null,"A","○","×",null,null,null,"○",null,"⑤","⑤","Ｂ",null,null,"低圧動力配電盤No.1の電流「〇〇」A",null,null,"ー","ー",{"$nulls":4},"電流"]
[{"$nulls":6},"検針",null,"電流",null,"A",null,null,null,"×",null,null,"×","⑤","⑤","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"電流"]
[{"$nulls":6},"検針","低圧動力配電盤No.2","電圧",null,"V","○","×",null,null,null,"○",null,"⑤","⑤","Ｂ",null,null,"低圧動力配電盤No.2の電圧「〇〇」V",null,null,"ー","ー",null,null,null,"低圧動力配電盤No.2","電圧"]
[{"$nulls":6},"検針","低圧動力配電盤No.2","電圧",null,"V",null,null,null,"×",null,null,"×","⑤","⑤","ー",{"$nulls":5},"ー","ー","ー",null,null,"低圧動力配電盤No.2","電圧"]
[{"$nulls":6},"検針",null,"電流",null,"A","○","×",null,null,null,"○",null,"⑤","⑤","Ｂ",null,null,"低圧動力配電盤No.2の電流「〇〇」A",null,null,"ー","ー",{"$nulls":4},"電流"]
[{"$nulls":6},"検針",null,"電流",null,"A",null,null,null,"×",null,null,"×","⑤","⑤","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"電流"]
[{"$nulls":6},"検針","電灯変圧器盤No.1","油温",null,"℃","○","×",null,null,null,"○",null,"⑤","⑤","Ｂ",null,null,"電灯変圧器盤No.1の油温「〇〇」℃",null,null,"ー","ー",null,null,null,"電灯変圧器盤No.1","油温"]
[{"$nulls":6},"検針","電灯変圧器盤No.1","油温",null,"℃",null,null,null,"×",null,null,"×","⑤","⑤","ー",{"$nulls":5},"ー","ー","ー",null,null,"電灯変圧器盤No.1","油温"]
[{"$nulls":6},"検針","電灯変圧器盤No.2","油温",null,"℃","○","×",null,null,null,"○",null,"⑤","⑤","Ｂ",null,null,"電灯変圧器盤No.2の油温「〇〇」℃",null,null,"ー","ー",null,null,null,"電灯変圧器盤No.2","油温"]
[{"$nulls":6},"検針","電灯変圧器盤No.2","油温",null,"℃",null,null,null,"×",null,null,"×","⑤","⑤","ー",{"$nulls":5},"ー","ー","ー",null,null,"電灯変圧器盤No.2","油温"]
[{"$nulls":6},"検針","動力変圧器盤No.1","油温",null,"℃","○","×",null,null,null,"○",null,"⑤","⑤","Ｂ",null,null,"動力変圧器盤No.1の油温「〇〇」℃",null,null,"ー","ー",null,null,null,"動力変圧器盤No.1","油温"]
[{"$nulls":6},"検針","動力変圧器盤No.1","油温",null,"℃",null,null,null,"×",null,null,"×","⑤","⑤","ー",{"$nulls":5},"ー","ー","ー",null,null,"動力変圧器盤No.1","油温"]
[{"$nulls":6},"検針","動力変圧器盤No.2","油温",null,"℃","○","×",null,null,null,"○",null,"⑤","⑤","Ｂ",null,null,"動力変圧器盤No.2の油温「〇〇」℃",null,null,"ー","ー",null,null,null,"動力変圧器盤No.2","油温"]
[{"$nulls":6},"検針","動力変圧器盤No.2","油温",null,"℃",null,null,null,"×",null,null,"×","⑤","⑤","ー",{"$nulls":5},"ー","ー","ー",null,null,"動力変圧器盤No.2","油温"]
[{"$nulls":6},"検針","非常動力電灯配電盤","T5 STR 主座 50VA/2 電圧",null,"V","○","×",null,null,null,"○",null,"⑤","⑤","Ｂ",null,null,"非常動力電灯配電盤のT5 STR 主座 50VA/2 電圧「〇〇」V",null,null,"ー","ー",null,null,null,"非常動力電灯配電盤","T5 STR 主座 50VA/2 電圧"]
[{"$nulls":6},"検針","非常動力電灯配電盤","T5 STR 主座 50VA/2 電圧",null,"V",null,null,null,"×",null,null,"×","⑤","⑤","ー",{"$nulls":5},"ー","ー","ー",null,null,"非常動力電灯配電盤","T5 STR 主座 50VA/2 電圧"]
[{"$nulls":6},"検針",null,"T5 STR 主座 50VA/2 電流",null,"A","○","×",null,null,null,"○",null,"⑤","⑤","Ｂ",null,null,"非常動力電灯配電盤のT5 STR 主座 50VA/2 電流「〇〇」A",null,null,"ー","ー",{"$nulls":4},"T5 STR 主座 50VA/2 電流"]
[{"$nulls":6},"検針",null,"T5 STR 主座 50VA/2 電流",null,"A",null,null,null,"×",null,null,"×","⑤","⑤","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"T5 STR 主座 50VA/2 電流"]
[{"$nulls":6},"検針",null,"T5 STR Ｔ座 50VA/2 電圧",null,"V","○","×",null,null,null,"○",null,"⑤","⑤","Ｂ",null,null,"非常動力電灯配電盤のT5 STR Ｔ座 50VA/2 電圧「〇〇」V",null,null,"ー","ー",{"$nulls":4},"T5 STR Ｔ座 50VA/2 電圧"]
[{"$nulls":6},"検針",null,"T5 STR Ｔ座 50VA/2 電圧",null,"V",null,null,null,"×",null,null,"×","⑤","⑤","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"T5 STR Ｔ座 50VA/2 電圧"]
[{"$nulls":6},"検針",null,"T5 STR Ｔ座 50VA/2 電流",null,"A","○","×",null,null,null,"○",null,"⑤","⑤","Ｂ",null,null,"非常動力電灯配電盤のT5 STR Ｔ座 50VA/2 電流「〇〇」A",null,null,"ー","ー",{"$nulls":4},"T5 STR Ｔ座 50VA/2 電流"]
[{"$nulls":6},"検針",null,"T5 STR Ｔ座 50VA/2 電流",null,"A",null,null,null,"×",null,null,"×","⑤","⑤","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"T5 STR Ｔ座 50VA/2 電流"]
[{"$nulls":6},"検針",null,"油温",null,"℃","○","×",null,null,null,"○",null,"⑤","⑤","Ｂ",null,null,"非常動力電灯配電盤の油温「〇〇」℃",null,null,"ー","ー",{"$nulls":4},"油温"]
[{"$nulls":6},"検針",null,"油温",null,"℃",null,null,null,"×",null,null,"×","⑤","⑤","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"油温"]
[{"$nulls":6},"設備点検","コンデンサ盤","異常",null,"有／無","○","×","○",null,null,"○",null,"⑤","⑤","A","無","有","コンデンサ盤に異常が無いこと",null,null,"ー","ー","ー",null,null,"コンデンサ盤","異常"]
[{"$nulls":5},"キュービクル","設備点検",null,"異音",null,"有／無","○","×",null,null,null,"○",null,"⑤","⑤","A","無","有","キュービクルに異音が無いこと",null,null,"ー","ー","ー",null,"キュービクル","キュービクル","異音"]
[{"$nulls":6},"設備点検",null,"異臭",null,"有／無","○","×",null,null,null,"○",null,"⑤","⑤","A","無","有","キュービクルに異臭が無いこと",null,null,"ー","ー","ー",null,null,null,"異臭"]
[{"$nulls":6},"設備点検","変圧器","油漏れ",null,"有／無","○","×","○",null,null,"○",null,"⑤","⑤","A","無","有","変圧器に油漏れが無いこと",null,null,"ー","ー","ー",null,null,"変圧器","油漏れ"]
[{"$nulls":6},"設備点検","コンデンサ","油漏れ",null,"有／無","○","×","○",null,null,"○",null,"⑤","⑤","A","無","有","コンデンサに油漏れが無いこと",null,null,"ー","ー","ー",null,null,"コンデンサ","油漏れ"]
[{"$nulls":6},"設備点検",null,"扉施錠",null,"有／無","○","×","○",null,null,"○",null,"⑤","⑤","A","施錠","開錠","コンデンサの扉が施錠されていること",null,null,"ー","ー","ー",null,null,"キュービクル","扉施錠"]
[{"$nulls":6},"設備点検",null,"制御電源表示灯",null,"点燈/消燈","○","×","○",null,null,"○",null,"⑤","⑤","A","点燈","消燈","コンデンサの制御電源表示灯が点燈していること",null,null,"ー","ー","ー",null,null,null,"制御電源表示灯"]
[null,null,"ｵﾌｨｽ棟","RF","屋上機器","空調機","設備点検",null,"異音",null,"有／無","○","×",null,null,null,"○",null,"⑤","⑤","A","無","有","空調機に異音が無いこと",null,null,"ー","ー","ー",null,"空調機","空調機","異音"]
[{"$nulls":6},"設備点検",null,"異臭",null,"有／無","○","×",null,null,null,"○",null,"⑤","⑤","A","無","有","空調機に異臭が無いこと",null,null,"ー","ー","ー",null,null,null,"異臭"]
[{"$nulls":6},"設備点検",null,"振動",null,"有／無","○","×","○",null,null,"○",null,"⑤","⑤","A","無","有","空調機に振動が無いこと",null,null,"ー","ー","ー",null,null,null,"振動"]
[{"$nulls":6},"設備点検","ケーシング","外観",null,"良／不","○","×","○",null,null,"○",null,"⑤","⑤","A","正常","異常","空調機のケーシング外観が正常であること",null,null,"ー","ー","ー",null,null,"ケーシング","外観"]
[{"$nulls":6},"設備点検","加圧シスターン","水漏れ",null,"有／無","○","×","○",null,null,"○",null,"⑤","⑤","A","無","有","空調機の加圧シスターンに水漏れが無いこと",null,null,"ー","ー","ー",null,null,"加圧シスターン","水漏れ"]
[{"$nulls":6},"検針","加湿ポンプ","圧力",null,"Mpa","○","×","○",null,null,"○",null,"⑤","⑤","Ｂ",null,null,"空調機の加湿ポンプの圧力「〇〇」Mpa",null,null,"ー","ー",null,null,null,"加湿ポンプ","圧力"]
[{"$nulls":6},"検針","加湿ポンプ","圧力(B)",null,"Mpa",null,null,null,"○",null,null,"○","⑤","⑤","Ｅ",{"$nulls":5},"ー","d775f29a-69d6-30c7-aebd-d259aabbc217-AI",null,null,null,"加湿ポンプ(B)","圧力(B)"]
[null,null,"ｵﾌｨｽ棟","RF","屋上機器","エコキュート","設備点検",null,"異音",null,"有／無","○","×",null,null,null,"○",null,"⑤","⑤","A","無","有","エコキュートに異音が無いこと",null,null,"ー","ー","ー",null,"エコキュート","エコキュート","異音"]
[{"$nulls":6},"設備点検",null,"異臭",null,"有／無","○","×",null,null,null,"○",null,"⑤","⑤","A","無","有","エコキュートに異臭が無いこと",null,null,"ー","ー","ー",null,null,null,"異臭"]
[{"$nulls":6},"設備点検","貯水槽","水漏れ",null,"有／無","○","×","○",null,null,"○",null,"⑤","⑤","A","無","有","エコキュートの貯水槽に水漏れが無いこと",null,null,"ー","ー","ー",null,null,"貯水槽","水漏れ"]
[{"$nulls":6},"設備点検","温水ポンプ","水漏れ",null,"有／無","○","×","○",null,null,"○",null,"⑤","⑤","A","無","有","エコキュートの温水ポンプに水漏れが無いこと",null,null,"ー","ー","ー",null,null,"温水ポンプ","水漏れ"]
[{"$nulls":6},"検針","循環ポンプ","1次側圧力",null,"Mpa","○","×","○",null,null,"○",null,"⑤","⑤","Ｂ",null,null,"エコキュートの循環ポンプの1次側圧力「〇〇」Mpa",null,null,"ー","ー",null,null,null,"循環ポンプ","1次側圧力"]
[{"$nulls":6},"検針","循環ポンプ","1次側圧力(B)",null,"Mpa",null,null,null,"○",null,null,"○","⑤","⑤","Ｅ",{"$nulls":5},"ー","7ee9b7b5-6674-3928-ab8d-bec313873d75-AI",null,null,null,"循環ポンプ(B)","1次側圧力(B)"]
[{"$nulls":6},"検針",null,"2次側圧力",null,"Mpa","○","×","○",null,null,"○",null,"⑤","⑤","Ｂ",null,null,"エコキュートの循環ポンプの2次側圧力「〇〇」Mpa",null,null,"ー","ー",{"$nulls":4},"2次側圧力"]
[{"$nulls":6},"検針",null,"2次側圧力(B)",null,"Mpa",null,null,null,"○",null,null,"○","⑤","⑤","Ｅ",{"$nulls":5},"ー","84bf8b4c-4418-33ec-a47f-f12f43da8221-AI",{"$nulls":4},"2次側圧力(B)"]
[null,null,"ｵﾌｨｽ棟","RF","屋上機器","給排気ファン","設備点検",null,"異音",null,"有／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,"給排気ファン",null,"異音"]
[{"$nulls":8},"異臭",null,"有／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"異臭"]
[{"$nulls":8},"振動",null,"有／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"振動"]
[{"$nulls":7},"Ｖベルト","滑り",null,"有／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,"Ｖベルト","滑り"]
[{"$nulls":7},"ダクト","破損",null,"有／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,"ダクト","破損"]
[null,null,"ｵﾌｨｽ棟","RF","屋上機器","低圧発電機","設備点検","発電機","制御電源表示灯",null,"点燈／消燈","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,"低圧発電機","発電機","制御電源表示灯"]
[{"$nulls":8},"腐食・さび",null,"有／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"腐食・さび"]
[{"$nulls":8},"油にじみ",null,"有／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"油にじみ"]
[{"$nulls":7},"燃料タンク","燃料漏れ",null,"有／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,"燃料タンク","燃料漏れ"]
[{"$nulls":8},"外観損傷",null,"有／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"外観損傷"]
[{"$nulls":8},"油にじみ",null,"有／無","×","×","×","×","×","×","×","×","×","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"油にじみ"]
[null,null,"ｵﾌｨｽ棟","RF","屋上機器","ネオン用タイマー","設備点検",null,"ケース破損",null,"有／無","○","×","○",null,null,"○",null,"⑤","⑤","A","無","有","ネオン用タイマーのケースに破損が無いこと",null,null,"ー","ー","ー",null,"ネオン用タイマー",null,"ケース破損"]
[{"$nulls":6},"設備点検",null,"異臭",null,"有／無","○","×",null,null,null,"○",null,"⑤","⑤","A","無","有","ネオン用タイマーに異臭が無いこと",null,null,"ー","ー","ー",null,null,null,"異臭"]
[{"$nulls":6},"設備点検",null,"時計",null,"正常／遅れ","○","×","○",null,null,"○",null,"⑤","⑤","A","正常","遅れ","ネオン用タイマーの時刻に正常であること",null,null,"ー","ー","ー",null,null,null,"時計"]
[{"$nulls":6},"設備点検",null,"配線焼損",null,"有／無","○","×","○",null,null,"○",null,"⑤","⑤","A","無","有","ネオン用タイマーの配線に焼損が無いこと",null,null,"ー","ー","ー",null,null,null,"配線焼損"]
[{"$nulls":6},"検針","ＲＦ","電源電圧",null,"V","○","×","○",null,null,"○",null,"⑤","⑤","Ｂ",null,null,"ネオン用タイマーのRFの電圧「〇〇」V",null,null,"ー","ー",null,null,null,"電源装置(ＲＦ)","電源電圧"]
[{"$nulls":6},"検針","ＲＦ","電源電圧(B)",null,"V",null,null,null,"○",null,null,"○","⑤","⑤","Ｅ",{"$nulls":5},"ー","d7ffc251-25e1-3e08-8a58-06c948234b32-AI",null,null,null,"電源装置(ＲＦ)(B)","電源電圧(B)"]
[{"$nulls":6},"検針","６ＲＦ","電源電圧",null,"V","○","×","○",null,null,"○",null,"⑤","⑤","Ｂ",null,null,"ネオン用タイマーの6RFの電圧「〇〇」V",null,null,"ー","ー",null,null,null,"電源装置(６ＲＦ)","電源電圧"]
[{"$nulls":6},"検針","６ＲＦ","電源電圧(B)",null,"V",null,null,null,"○",null,null,"○","⑤","⑤","Ｅ",{"$nulls":5},"ー","71efcd8f-4848-3a9e-b279-b11dea1dbf0e-AI",null,null,null,"電源装置(６ＲＦ)(B)","電源電圧(B)"]
[null,null,"ｵﾌｨｽ棟","RF","屋上機器","消火補給水槽","設備点検","バルブ","水漏れ",null,"有／無","○","○","○",null,null,"○",null,"⑤","⑤","A","無","有","消火補給水槽のバルブに水漏れが無いこと",null,null,"ー","ー","ー",null,"消火補給水槽","バルブ","水漏れ"]
[{"$nulls":6},"設備点検","ボールタップ","動作",null,"正常／異常","○","○","○",null,null,"○",null,"⑤","⑤","A","正常","異常","消火補給水槽のボールタップが正常であること",null,null,"ー","ー","ー",null,null,"ボールタップ","動作"]
[{"$nulls":6},"設備点検","水槽","外観",null,"正常／異常","○","○","○",null,null,"○",null,"⑤","⑤","A","正常","異常","消火補給水槽の外観が正常であること",null,null,"ー","ー","ー",null,null,"水槽","外観"]
[{"$nulls":6},"設備点検","配管","漏れ・腐食",null,"有／無","○","○","○",null,null,"○",null,"⑤","⑤","A","無","有","消火補給水槽の配管に漏れ・腐食が無いこと",null,null,"ー","ー","ー",null,null,"配管","漏れ・腐食"]
[{"$nulls":6},"設備点検",null,"防虫網",null,"有／無","○","○","○",null,null,"○",null,"⑤","⑤","A","有","無","消火補給水槽の配管に防虫網が有ること",null,null,"ー","ー","ー",null,null,null,"防虫網"]
[null,null,"実験棟","6RF","屋上機器","サブキュービクル","検針","高圧受電盤","受電電圧",null,"V","○","○","○",null,null,"○",null,"⑥","⑥","Ｂ",null,null,"高圧受電盤の電圧「〇〇」V",null,null,"ー","ー",null,null,"サブキュービクル","高圧受電盤","受電電圧"]
[{"$nulls":6},"検針","高圧受電盤","受電電圧(B)",null,"V",null,null,null,"○",null,null,"○","⑥","⑥","Ｅ",{"$nulls":5},"ー","bc366b7b-8d5c-3892-9b88-806e1e1caf48-AI",null,null,null,"高圧受電盤(B)","受電電圧(B)"]
[{"$nulls":6},"検針",null,"電流値",null,"A","○","○","○",null,null,"○",null,"⑥","⑥","Ｂ",null,null,"高圧受電盤の電流「〇〇」A",null,null,"ー","ー",{"$nulls":4},"電流値"]
[{"$nulls":6},"検針",null,"電流値(B)",null,"A",null,null,null,"○",null,null,"○","⑥","⑥","Ｅ",{"$nulls":5},"ー","5883c803-f6d6-3bba-9c04-b2a9e39456b8-AI",{"$nulls":4},"電流値(B)"]
[{"$nulls":6},"検針","高圧引き込み盤","電力量",null,"KWH","○","○","○",null,null,"○",null,"⑥","⑥","Ｂ",null,null,"高圧引き込み盤の電力量「〇〇」KWH",null,null,"ー","ー",null,null,null,"高圧引き込み盤","電力量"]
[{"$nulls":6},"検針","高圧引き込み盤","電力量(B)",null,"KWH",null,null,null,"○",null,null,"○","⑥","⑥","Ｅ",{"$nulls":5},"ー","6276e229-3741-3899-86be-f24b77b1f315-AI",null,null,null,"高圧引き込み盤(B)","電力量(B)"]
[{"$nulls":6},"検針","低圧電灯配電盤","電圧",null,"V","○","○","○",null,null,"○",null,"⑥","⑥","Ｂ",null,null,"低圧電灯配電盤の電圧「〇〇」V",null,null,"ー","ー",null,null,null,"低圧電灯配電盤","電圧"]
[{"$nulls":6},"検針","低圧電灯配電盤","電圧(B)",null,"V",null,null,null,"○",null,null,"○","⑥","⑥","Ｅ",{"$nulls":5},"ー","d05f17d7-0370-3cbf-95e6-44f430bf1268-AI",null,null,null,"低圧電灯配電盤(B)","電圧(B)"]
[{"$nulls":6},"検針",null,"電流",null,"A","○","○","○",null,null,"○",null,"⑥","⑥","Ｂ",null,null,"低圧電灯配電盤の電流「〇〇」A",null,null,"ー","ー",{"$nulls":4},"電流"]
[{"$nulls":6},"検針",null,"電流(B)",null,"A",null,null,null,"○",null,null,"○","⑥","⑥","Ｅ",{"$nulls":5},"ー","b38bae4d-1af1-3321-95c4-d93659845eb0-AI",{"$nulls":4},"電流(B)"]
[{"$nulls":6},"検針","低圧動力配電盤No.1","電圧",null,"V","○","×","○",null,null,"○",null,"⑥","⑥","Ｂ",null,null,"低圧動力配電盤No.1の電圧「〇〇」V",null,null,"ー","ー",null,null,null,"低圧動力配電盤No.1","電圧"]
[{"$nulls":6},"検針","低圧動力配電盤No.1","電圧",null,"V",null,null,null,"×",null,null,"×","⑥","⑥","ー",{"$nulls":5},"ー","ー","ー",null,null,"低圧動力配電盤No.1","電圧"]
[{"$nulls":6},"検針",null,"電流",null,"A","○","×","○",null,null,"○",null,"⑥","⑥","Ｂ",null,null,"低圧動力配電盤No.1の電流「〇〇」A",null,null,"ー","ー",{"$nulls":4},"電流"]
[{"$nulls":6},"検針",null,"電流",null,"A",null,null,null,"×",null,null,"×","⑥","⑥","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"電流"]
[{"$nulls":6},"検針","低圧動力配電盤No.2","電圧",null,"V","○","×","○",null,null,"○",null,"⑥","⑥","Ｂ",null,null,"低圧動力配電盤No.2の電圧「〇〇」V",null,null,"ー","ー",null,null,null,"低圧動力配電盤No.2","電圧"]
[{"$nulls":6},"検針","低圧動力配電盤No.2","電圧",null,"V",null,null,null,"×",null,null,"×","⑥","⑥","ー",{"$nulls":5},"ー","ー","ー",null,null,"低圧動力配電盤No.2","電圧"]
[{"$nulls":6},"検針",null,"電流",null,"A","○","×","○",null,null,"○",null,"⑥","⑥","Ｂ",null,null,"低圧動力配電盤No.2の電流「〇〇」A",null,null,"ー","ー",{"$nulls":4},"電流"]
[{"$nulls":6},"検針",null,"電流",null,"A",null,null,null,"×",null,null,"×","⑥","⑥","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"電流"]
[{"$nulls":6},"検針","低圧動力配電盤No.3(420V)","電圧",null,"V","○","×","○",null,null,"○",null,"⑥","⑥","Ｂ",null,null,"低圧動力配電盤No.3(420V)の電圧「〇〇」V",null,null,"ー","ー",null,null,null,"低圧動力配電盤No.3(420V)","電圧"]
[{"$nulls":6},"検針","低圧動力配電盤No.3(420V)","電圧",null,"V",null,null,null,"×",null,null,"×","⑥","⑥","ー",{"$nulls":5},"ー","ー","ー",null,null,"低圧動力配電盤No.3(420V)","電圧"]
[{"$nulls":6},"検針",null,"電流",null,"A","○","×","○",null,null,"○",null,"⑥","⑥","Ｂ",null,null,"低圧動力配電盤No.3(420V)の電流「〇〇」A",null,null,"ー","ー",{"$nulls":4},"電流"]
[{"$nulls":6},"検針",null,"電流",null,"A",null,null,null,"×",null,null,"×","⑥","⑥","ー",{"$nulls":5},"ー","ー","ー",null,null,null,"電流"]
[{"$nulls":6},"検針","電灯変圧器盤","油温",null,"℃","○","×","○",null,null,"○",null,"⑥","⑥","Ｂ",null,null,"電灯変圧器盤の油圧「〇〇」℃",null,null,"ー","ー",null,null,null,"電灯変圧器盤","油温"]
[{"$nulls":6},"検針","電灯変圧器盤","油温",null,"℃",null,null,null,"×",null,null,"×","⑥","⑥","ー",{"$nulls":5},"ー","ー","ー",null,null,"電灯変圧器盤","油温"]
[{"$nulls":6},"検針","動力変圧器盤No.1","油温",null,"℃","○","×","○",null,null,"○",null,"⑥","⑥","Ｂ",null,null,"動力変圧器盤No.1の油圧「〇〇」℃",null,null,"ー","ー",null,null,null,"動力変圧器盤No.1","油温"]
[{"$nulls":6},"検針","動力変圧器盤No.1","油温",null,"℃",null,null,null,"×",null,null,"×","⑥","⑥","ー",{"$nulls":5},"ー","ー","ー",null,null,"動力変圧器盤No.1","油温"]
[{"$nulls":6},"検針","動力変圧器盤No.2","油温",null,"℃","○","×","○",null,null,"○",null,"⑥","⑥","Ｂ",null,null,"動力変圧器盤No.2の油圧「〇〇」℃",null,null,"ー","ー",null,null,null,"動力変圧器盤No.2","油温"]
[{"$nulls":6},"検針","動力変圧器盤No.2","油温",null,"℃",null,null,null,"×",null,null,"×","⑥","⑥","ー",{"$nulls":5},"ー","ー","ー",null,null,"動力変圧器盤No.2","油温"]
[{"$nulls":6},"検針","動力変圧器盤No.3(420V)","油温",null,"℃","○","×","○",null,null,"○",null,"⑥","⑥","Ｂ",null,null,"動力変圧器盤No.3(420V)の油圧「〇〇」℃",null,null,"ー","ー",null,null,null,"動力変圧器盤No.3(420V)","油温"]
[{"$nulls":6},"検針","動力変圧器盤No.3(420V)","油温",null,"℃",null,null,null,"×",null,null,"×","⑥","⑥","ー",{"$nulls":5},"ー","ー","ー",null,null,"動力変圧器盤No.3(420V)","油温"]
[{"$nulls":6},"設備点検","コンデンサ盤","異常",null,"有／無","○","×","○",null,null,"○",null,"⑥","⑥","A","無","有","コンデンサ盤に異常が無いこと",null,null,"ー","ー","ー",null,null,"コンデンサ盤","異常"]
[null,null,"実験棟","6RF","屋上機器","空調機","設備点検",null,"異音",null,"有／無","○","×",null,null,null,"○",null,"⑥","⑥","A","無","有","空調機に異音が無いこと",null,null,"ー","ー","ー",null,"空調機","空調機","異音"]
[{"$nulls":6},"設備点検",null,"異臭",null,"有／無","○","×",null,null,null,"○",null,"⑥","⑥","A","無","有","空調機に異臭が無いこと",null,null,"ー","ー","ー",null,null,null,"異臭"]
[{"$nulls":6},"設備点検",null,"振動",null,"有／無","○","×",null,null,null,"○",null,"⑥","⑥","A","無","有","空調機に振動が無いこと",null,null,"ー","ー","ー",null,null,null,"振動"]
[{"$nulls":6},"設備点検","ケーシング","外観",null,"良／不","○","×",null,null,null,"○",null,"⑥","⑥","A","正常","異常","空調機のケーシングの外観が正常であること",null,null,"ー","ー","ー",null,null,"空調機　ケーシング","外観"]
[{"$nulls":6},"設備点検","加圧シスターン","水漏れ",null,"有／無","○","×",null,null,null,"○",null,"⑥","⑥","A","無","有","空調機の加圧シスターンの水漏れが無いこと",null,null,"ー","ー","ー",null,null,"空調機　加圧シスターン","水漏れ"]
[{"$nulls":6},"検針","加湿ポンプ","圧力",null,"Mpa","○","×",null,null,null,"○",null,"⑥","⑥","Ｂ",null,null,"空調機の加湿ポンプの圧力「〇〇」Mpa",null,null,"ー","ー",null,null,null,"空調機　加湿ポンプ","圧力"]
[{"$nulls":6},"検針","加湿ポンプ","圧力(B)",null,"Mpa",null,null,null,"○",null,null,"○","⑥","⑥","Ｅ",{"$nulls":5},"ー","9bfc770a-2cb9-3efe-85e5-50bf89cf790a-AI",null,null,null,"空調機　加湿ポンプ(B)","圧力(B)"]
[null,null,"実験棟","6RF","屋上機器","屋上植栽散水装置","設備点検","ボールタップ","動作",null,"正常／異常","○","×","○",null,null,"○",null,"⑦","⑦","A","正常","異常","屋上植栽散水装置のボールタップの動作が正常であること",null,null,"ー","ー","ー",null,"屋上植栽散水装置","ボールタップ","動作"]
[{"$nulls":6},"設備点検","タンク・ホース","水漏れ",null,"有／無","○","×","○",null,null,"○",null,"⑦","⑦","A","無","有","屋上植栽散水装置のタンク・ホースの水漏れが無いこと",null,null,"ー","ー","ー",null,null,"タンク・ホース","水漏れ"]
[{"$nulls":6},"設備点検","給水ポンプ","異音",null,"有／無","○","×",null,null,null,"○",null,"⑦","⑦","A","無","有","屋上植栽散水装置の給水ポンプから異音が無いこと",null,null,"ー","ー","ー",null,null,"給水ポンプ","異音"]
[{"$nulls":6},"設備点検",null,"異臭",null,"有／無","○","×",null,null,null,"○",null,"⑦","⑦","A","無","有","屋上植栽散水装置の給水ポンプから異臭が無いこと",null,null,"ー","ー","ー",null,null,null,"異臭"]
[{"$nulls":6},"検針","灌水制御盤","1・2系統電圧",null,"V","○","×","○",null,null,"○",null,"⑦","⑦","Ｂ",null,null,"屋上植栽散水装置の灌水制御盤の1・2系統電圧「〇〇」V",null,null,"ー","ー",null,null,null,"灌水制御盤","1・2系統電圧"]
[{"$nulls":6},"検針","灌水制御盤","1・2系統電圧(B)",null,"V",null,null,null,"○",null,null,"○","⑦","⑦","Ｅ",{"$nulls":5},"ー","58417b3c-c99c-3881-b071-308847ed2496-AI",null,null,null,"灌水制御盤(B)","1・2系統電圧(B)"]
[{"$nulls":6},"検針",null,"3・4系統電圧",null,"V","○","×","○",null,null,"○",null,"⑦","⑦","Ｂ",null,null,"屋上植栽散水装置の灌水制御盤の3・4系統電圧「〇〇」V",null,null,"ー","ー",{"$nulls":4},"3・4系統電圧"]
[{"$nulls":6},"検針",null,"3・4系統電圧(B)",null,"V",null,null,null,"○",null,null,"○","⑦","⑦","Ｅ",{"$nulls":5},"ー","cc10bec3-b7f8-321b-8335-9a4d6512e7e2-AI",{"$nulls":4},"3・4系統電圧(B)"]
[null,null,"ｵﾌｨｽ棟","1F","EPS","雨水ポンプ","計測","センサ１","水位",null,"A",{"$nulls":4},"○",null,"○","ー","④","Ｃ",{"$nulls":5},"WLL2ZT92","4F02113B",null,null,"雨水ポンプ","雨水ポンプ　貯水槽","水位"]
[null,null,"ｵﾌｨｽ棟","7F","C708会議室","換気","計測","センサ１","温湿度",null,"℃、％",{"$nulls":4},"○",null,"○","ー","⑧","Ｃ",{"$nulls":5},"NBI-WM0203","BF0004E8",null,null,"環境","環境センサＡ","温湿度"]
[{"$nulls":6},"計測",null,"照度",null,"lux",{"$nulls":4},"○",null,"○","ー","⑧","Ｃ",{"$nulls":11},"照度"]
[{"$nulls":6},"計測","センサ２","CO2",null,"ppm",{"$nulls":4},"○",null,"○","ー","⑧","Ｃ",{"$nulls":5},"SZC100","BF0010B9",null,null,null,"環境センサＢ","CO2"]
[{"$nulls":6},"計測",null,"温度",null,"℃",{"$nulls":4},"○",null,"○","ー","⑧","Ｃ",{"$nulls":11},"温度"]
[{"$nulls":6},"計測",null,"湿度",null,"％",{"$nulls":4},"○",null,"○","ー","⑧","Ｃ",{"$nulls":11},"湿度"]
[{"$nulls":6},"状態","センサ３","ドアセンサ",null,"開／閉",{"$nulls":4},"○",null,"○","ー","⑧","Ｃ","閉","開",null,null,null,"DMZ4ZT92","4F00E228",null,null,null,"C708会議室ドア","ドアセンサ"]
[{"$nulls":6},"状態","センサ４","人感",null,"在／不在",{"$nulls":4},"○",null,"○","ー","⑧","Ｃ","不在","在",null,null,null,"IRZ1ZT92","4F00ABB5",null,null,null,"C708会議室人感","人感"]
[null,null,"ｵﾌｨｽ棟","7F","執務室","ゴミ箱１","計測","センサ１","超音波距離",null,"cm",{"$nulls":4},"○",null,"○","ー","⑨","Ｃ",{"$nulls":5},"JZUS91A1","BF001028",null,null,"衛生","ゴミ箱１","超音波距離"]
[{"$nulls":5},"ゴミ箱２","計測","センサ１","超音波距離",null,"cm",{"$nulls":4},"○",null,"○","ー","⑨","Ｃ",{"$nulls":5},"JZUS91A1","BF001029",null,null,null,"ゴミ箱２","超音波距離"]
[{"$nulls":5},"ゴミ箱３","計測","センサ１","超音波距離",null,"cm",{"$nulls":4},"○",null,"○","ー","⑨","Ｃ",{"$nulls":5},"JZUS91A1","BF001032",null,null,null,"ゴミ箱３","超音波距離"]
[null,null,"ｵﾌｨｽ棟","7F","備品倉庫","台車１","状態","センサ１","無:0:ALM　有:1:NMR",null,"有／無",{"$nulls":4},"○",null,"○","ー","⑩","Ｃ","有","無",{"$nulls":7},"備品","台車１","無:0:ALM　有:1:NMR"]
[{"$nulls":5},"台車２","状態","センサ２","無:0:ALM　有:1:NMR",null,"有／無",{"$nulls":4},"○",null,"○","ー","⑩","Ｃ","有","無",{"$nulls":8},"台車２","無:0:ALM　有:1:NMR"]
[{"$nulls":5},"台車３","状態","センサ２","無:0:ALM　有:1:NMR",null,"有／無",{"$nulls":4},"○",null,"○","ー","⑩","Ｃ","有","無",{"$nulls":8},"台車３","無:0:ALM　有:1:NMR"]
[{"$nulls":5},"脚立１","状態","センサ２","無:0:ALM　有:1:NMR",null,"有／無",{"$nulls":4},"○",null,"○","ー","⑩","Ｃ","有","無",{"$nulls":8},"脚立１","無:0:ALM　有:1:NMR"]
[{"$nulls":5},"脚立２","状態","センサ２","無:0:ALM　有:1:NMR",null,"有／無",{"$nulls":4},"○",null,"○","ー","⑩","Ｃ","有","無",{"$nulls":8},"脚立２","無:0:ALM　有:1:NMR"]
[{"$nulls":5},"脚立３","状態","センサ３","無:0:ALM　有:1:NMR",null,"有／無",{"$nulls":4},"○",null,"○","ー","⑩","Ｃ","有","無",{"$nulls":8},"脚立３","無:0:ALM　有:1:NMR"]
[null,null,"実験棟","4F","廊下","照明","計測","センサ１","照度",null,"lux",{"$nulls":4},"○",null,"○","ー","⑪","Ｃ",{"$nulls":5},"OPZ1ZT92","4F009CC7",null,null,"照明","照明","照度"]
[null,null,"実験棟","4F","ｻｰﾊﾞｰﾙｰﾑ","温度","計測","センサ２","温度",null,"℃",{"$nulls":4},"○",null,"○","ー","⑫","Ｃ",{"$nulls":5},"THZ2ZT92","4F00CA48",null,null,"環境","環境センサＣ","温度"]
[{"$nulls":6},"計測",null,"湿度",null,"％",{"$nulls":4},"○",null,"○","ー","⑫","Ｃ",{"$nulls":11},"湿度"]
[{"$nulls":6},"計測","センサ３","温度(接触)",null,"℃",{"$nulls":4},"○",null,"○","ー","⑫","Ｃ",{"$nulls":5},"TZZTZT92","4F00A926",null,null,null,"接触温度計","温度(接触)"]
[{"$nulls":6},"計測","センサ４","温度(接触)",null,"℃",{"$nulls":4},"○",null,"○","ー","⑫","Ｃ",{"$nulls":5},"TZZTZT92","4F00A928",null,null,null,"接触温度計","温度(接触)"]
[{"$nulls":6},"計測","センサ５","電流センサ",null,"A",{"$nulls":4},"○",null,"○","ー","⑫","Ｃ",{"$nulls":5},"CRACZT92","4F00E1D9",null,null,null,"消費電流計","電流センサ"]
[null,null,"実験棟","4F","ﾜｰｸｽﾍﾟｰｽ",null,"計測","センサ１","温湿度",null,"℃、％",{"$nulls":4},"○",null,"○","ー","⑬","Ｃ",{"$nulls":5},"NBI-WM0203","BF000BE5",null,null,"環境","環境センサＤ","温湿度"]
[{"$nulls":4},"実験室２",null,"計測",null,"照度",null,"lux",{"$nulls":4},"○",null,"○","ー","⑬","Ｃ",{"$nulls":11},"照度"]
[{"$nulls":6},"状態","センサ２","人感",null,"在／不在",{"$nulls":4},"○",null,"○","ー","⑬","Ｃ","不在","在",null,null,null,"IRZ1ZT92","4F00AA3D",null,null,null,"実験室２人感","人感"]
[null,null,"実験棟","6RF","屋上緑化","土壌","計測","センサ１","超音波流量",null,"L/min",{"$nulls":4},"○",null,"○","ー","⑦","Ｃ",{"$nulls":5},"D4ACZT92","4F00E1B7",null,null,"環境","灌水ポンプ","超音波流量"]
[{"$nulls":5},"土壌","計測","センサ１","土壌温度",null,"℃、％",{"$nulls":4},"○",null,"○","ー","⑭","Ｃ",{"$nulls":5},"NBI-WP0403","BF0004F4",null,null,"環境","土壌","土壌温度"]
[{"$nulls":6},"計測",null,"土壌水分量",null,"誘電率",{"$nulls":4},"○",null,"○","ー","⑭","Ｃ",{"$nulls":5},"NBI-WP0403","BF0004F4",{"$nulls":4},"土壌水分量"]
[{"$nulls":6},"計測",null,"土壌pH",null,"pH",{"$nulls":4},"○",null,"○","ー","⑭","Ｃ",{"$nulls":5},"NBI-WP0403","BF0004F4",{"$nulls":4},"土壌pH"]
[{"$nulls":6},"計測",null,"土壌EC",null,"dS/m、℃",{"$nulls":4},"○",null,"○","ー","⑭","Ｃ",{"$nulls":5},"NBI-WP0403","BF0004F4",{"$nulls":4},"土壌EC"]
[{"$nulls":6},"計測",null,"葉面温度",null,"℃",{"$nulls":4},"○",null,"○","ー","⑭","Ｃ",{"$nulls":5},"NBI-WP0403","BF0004F4",{"$nulls":4},"葉面温度"]
[{"$nulls":6},"計測",null,"葉面湿度",null,"％",{"$nulls":4},"○",null,"○","ー","⑭","Ｃ",{"$nulls":5},"NBI-WP0403","BF0004F4",{"$nulls":4},"葉面湿度"]
[{"$nulls":6},"計測",null,"光合成有効放射",null,"μmol/m2•s",{"$nulls":4},"○",null,"○","ー","⑭","Ｃ",{"$nulls":5},"NBI-WP0403","BF0004F4",{"$nulls":4},"光合成有効放射"]
[{"$nulls":6},"計測",null,"気温",null,"℃",{"$nulls":4},"○",null,"○","ー","⑭","Ｃ",{"$nulls":5},"NBI-WP0403","BF0004F4",{"$nulls":4},"気温"]
[{"$nulls":6},"計測",null,"湿度",null,"％",{"$nulls":4},"○",null,"○","ー","⑭","Ｃ",{"$nulls":5},"NBI-WP0403","BF0004F4",{"$nulls":4},"湿度"]
[{"$nulls":6},"計測",null,"照度",null,"lux",{"$nulls":4},"○",null,"○","ー","⑭","Ｃ",{"$nulls":5},"NBI-WP0403","BF0004F4",{"$nulls":4},"照度"]
[null,null,"屋外","3F","鉄塔","傾斜","計測","センサ１","傾斜",null,"度",{"$nulls":4},"○",null,"○","ー","⑮","Ｃ",{"$nulls":5},"SZT200","BF0010B2",null,null,"環境","傾斜","傾斜"]
[{"$nulls":5},"気象(屋上)","計測","センサ２","風向",null,"0°- 359°",{"$nulls":4},"○",null,"○","ー","⑮","Ｃ",{"$nulls":5},"SZW100","BF0010B6",null,null,"環境","気象(RF)","風向"]
[{"$nulls":6},"計測",null,"風速",null,"m/s",{"$nulls":4},"○",null,"○","ー","⑮","Ｃ",{"$nulls":11},"風速"]
[{"$nulls":6},"計測",null,"瞬間風速",null,"m/s",{"$nulls":4},"○",null,"○","ー","⑮","Ｃ",{"$nulls":11},"瞬間風速"]
[{"$nulls":6},"計測",null,"温度",null,"℃",{"$nulls":4},"○",null,"○","ー","⑮","Ｃ",{"$nulls":11},"温度"]
[{"$nulls":6},"計測",null,"湿度",null,"％",{"$nulls":4},"○",null,"○","ー","⑮","Ｃ",{"$nulls":11},"湿度"]
[{"$nulls":6},"計測",null,"照度",null,"lux",{"$nulls":4},"○",null,"○","ー","⑮","Ｃ",{"$nulls":11},"照度"]
[{"$nulls":6},"計測",null,"雨量",null,"mm",{"$nulls":4},"○",null,"○","ー","⑮","Ｃ",{"$nulls":11},"雨量"]
[{"$nulls":6},"計測",null,"紫外線量",null,"μW/㎠",{"$nulls":4},"○",null,"○","ー","⑮","Ｃ",{"$nulls":11},"紫外線量"]
[null,null,"屋外","1F","鉄塔","気象(地上)","計測","センサ３","風向",null,"0°- 359°",{"$nulls":4},"○",null,"○","ー","⑯","Ｃ",{"$nulls":5},"SZW100","BF0010B7",null,null,"環境","気象(GL)","風向"]
[{"$nulls":6},"計測",null,"風速",null,"m/s",{"$nulls":4},"○",null,"○","ー","⑯","Ｃ",{"$nulls":11},"風速"]
[{"$nulls":6},"計測",null,"瞬間風速",null,"m/s",{"$nulls":4},"○",null,"○","ー","⑯","Ｃ",{"$nulls":11},"瞬間風速"]
[{"$nulls":6},"計測",null,"温度",null,"℃",{"$nulls":4},"○",null,"○","ー","⑯","Ｃ",{"$nulls":11},"温度"]
[{"$nulls":6},"計測",null,"湿度",null,"％",{"$nulls":4},"○",null,"○","ー","⑯","Ｃ",{"$nulls":11},"湿度"]
[{"$nulls":6},"計測",null,"照度",null,"lux",{"$nulls":4},"○",null,"○","ー","⑯","Ｃ",{"$nulls":11},"照度"]
[{"$nulls":6},"計測",null,"雨量",null,"mm",{"$nulls":4},"○",null,"○","ー","⑯","Ｃ",{"$nulls":11},"雨量"]
[{"$nulls":6},"計測",null,"紫外線量",null,"μW/㎠",{"$nulls":4},"○",null,"○","ー","⑯","Ｃ",{"$nulls":11},"紫外線量"]
[null,null,"屋外","1F","倉庫",null,"計測","センサ１","温度",null,"℃",{"$nulls":4},"○",null,"○","ー","⑰","Ｃ",{"$nulls":5},"THZ2ZT92","4F00CA49",null,null,null,"環境センサＥ","温度"]
[{"$nulls":6},"計測",null,"湿度",null,"％",{"$nulls":4},"○",null,"○","ー","⑰","Ｃ",{"$nulls":11},"湿度"]
[null,null,"ｵﾌｨｽ棟","RF","屋上機器","キュービクル","計測","高圧受電盤２","電流２",null,"A",{"$nulls":4},"○",null,"○","ー","○","Ｄ",{"$nulls":5},"CRACZT92","4F00E1DB",null,null,"キュービクル","高圧受電盤２","電流２"]
[null,null,"ｵﾌｨｽ棟","１Ｆ","消火ポンプ室",null,"状態",null,"ドアセンサ",null,"開／閉",{"$nulls":4},"○",null,"○","ー","○","Ｄ","閉","開",null,null,null,"DMZ4ZT92","4F00E229",null,null,null,"消火ポンプ室　ドア","ドアセンサ"]
[null,null,"ｵﾌｨｽ棟","１Ｆ","消火ポンプ室","泡消火栓ポンプ","状態","泡消火栓ポンプ１","ドライ接点センサー",null,"運転／停止",{"$nulls":4},"○",null,"○","ー","○","Ｄ","停止","運転",null,null,null,"OCZ1ZT92","4F007A13",null,null,"泡消火栓ポンプ","泡消火栓　ポンプ１","ドライ接点センサー"]
[null,null,"ｵﾌｨｽ棟","１Ｆ","消火ポンプ室",null,"状態","泡消火栓ポンプ２","運転状態",null,"運転／停止",{"$nulls":4},"○",null,"○","ー","○","Ｄ","停止","運転",null,null,null,"OC16ZT92","4F020A43",null,null,null,"泡消火栓　ポンプ２","運転状態"]
[null,null,"ｵﾌｨｽ棟","１Ｆ","消火ポンプ室",null,"状態","泡消火栓ポンプ３","運転状態",null,"運転／停止",{"$nulls":4},"○",null,"○","ー","○","Ｄ","停止","運転",{"$nulls":8},"泡消火栓　ポンプ３","運転状態"]
[null,null,"ｵﾌｨｽ棟","１Ｆ","消火ポンプ室","泡消火栓ポンプ","状態","消火栓ポンプ２","漏水(接点)",null,"正常／漏水",{"$nulls":4},"○",null,"○","ー","②","Ｄ","正常","漏水",null,null,null,"WDZ1ZT92","4F00A904",null,null,null,"泡消火栓　ポンプ１","漏水(接点)"]
[null,null,"ｵﾌｨｽ棟","１Ｆ","消火ポンプ室","消火栓ポンプ","状態","火栓ポンプ２","漏水(ｹｰﾌﾞﾙ)",null,"正常／漏水",{"$nulls":4},"○",null,"○","ー","②","Ｄ","正常","漏水",null,null,null,"WDZ3ZT92-1","4F00AAF9",null,null,"消火栓ポンプ","消火栓　ポンプ１","漏水(ｹｰﾌﾞﾙ)"]
[null,null,"ｵﾌｨｽ棟","RF","屋上機器","キュービクル","計測","高圧受電盤２","電圧",null,"V",{"$nulls":4},"○",null,"○","ー","⑤","Ｄ",{"$nulls":5},"D485ZT92","4F00CA19",null,null,"キュービクル","高圧受電盤２","電圧"]
[{"$nulls":6},"計測",null,"電流",null,"A",{"$nulls":4},"○",null,"○","ー","○","Ｄ",{"$nulls":11},"電流"]
[{"$nulls":6},"計測",null,"瞬間電力",null,"W",{"$nulls":4},"○",null,"○","ー","○","Ｄ",{"$nulls":11},"瞬間電力"]
[{"$nulls":6},"計測",null,"積算電量量",null,"A",{"$nulls":4},"○",null,"○","ー","○","Ｄ",{"$nulls":11},"積算電量量"]
[]
[{"$nulls":30},"電気通信設備","E:SYMデータに関する"]
[{"$nulls":30},"　受変電設備","設備名称は(B)を付加する"]
[{"$nulls":30},"　屋内配線設備","(DBMでデータ入力の異なる"]
[{"$nulls":30},"　照明設備","設備名は同一で扱えない)"]
[{"$nulls":30},"　非常用電源設備"]
[{"$nulls":30},"　電話設備"]
[{"$nulls":30},"　蓄電池設備"]
[{"$nulls":30},"空気調和設備"]
[{"$nulls":30},"　ボイラー"]
[{"$nulls":23},"Ａ：設備点検情報　スマホからDBMへ状態を送信",{"$nulls":6},"　空気調和装置"]
[{"$nulls":23},"Ｂ：検針情報　　　スマホからDBMへ数値を送信",{"$nulls":6},"　冷凍機・冷却塔"]
[{"$nulls":23},"Ｃ：検針情報　　　ZETAからDBMへ状態／数値を計測",{"$nulls":6},"　冷温水発生器"]
[{"$nulls":23},"D1：検針情報　　　ZETAからDBMへ状態／数値を計測",{"$nulls":6},"　送風機・排風機"]
[{"$nulls":23},"D2：検針情報　　　ZETAからButicsAXへ状態／数値を計測",{"$nulls":6},"給排水設備"]
[{"$nulls":23},"Ｅ：検針情報　　　SYMからDBMへ状態／数値を計測",{"$nulls":6},"消防設備"]
[{"$nulls":30},"　警報装置"]
[{"$nulls":30},"　消火設備"]
[{"$nulls":30},"　避難設備"]
[{"$nulls":30},"昇降機設備"]
[{"$nulls":30},"　エスカレータ"]
[{"$nulls":30},"　エレベータ"]

{"sheet":"传感器列表","index":1,"n_rows":64,"n_cols":14,"rows_kept":64,"cut":false,"hidden":false,"merged":[[1,0,63,0],[1,1,63,1],[2,6,4,6],[5,6,7,6],[10,6,12,6],[14,6,15,6],[16,6,17,6],[19,6,21,6],[24,6,33,6],[35,6,42,6],[43,6,50,6],[51,6,52,6],[56,6,57,6],[60,6,63,6],[2,7,4,7],[5,7,7,7],[14,7,15,7],[19,7,21,7],[24,7,33,7],[35,7,42,7],[43,7,50,7],[51,7,52,7],[56,7,57,7],[60,7,63,7],[2,8,4,8],[5,8,7,8],[14,8,15,8],[19,8,21,8],[35,8,42,8],[43,8,50,8],[51,8,52,8],[56,8,57,8],[60,8,63,8]]}
["租户","项目","大楼","楼层","空间","资产","传感器种类","型号","ID","指标","英文","字段","指标 id","单位"]
["NECネッツエスアイ株式会社","KTC","ｵﾌｨｽ棟","1F","EPS","雨水ポンプ　貯水槽","ZETA 水位传感器","WLL2ZT92","4F02113B","水位","water_level","4F02113B_water_level","2a58644283d64929b658f050a758c90c","A"]
[null,null,"ｵﾌｨｽ棟","7F","C708会議室","環境センサＡ","NBI WatcherMini2\n1035183078120000 ","NBI-WM0203","BF0004E8","温度","temperature","BF0004E8_temperature","43656ef5838a4834bce7838f564fd803","℃、％"]
[null,null,"ｵﾌｨｽ棟","7F","C708会議室","環境センサＡ",null,null,null,"湿度","humidity","BF0004E8_humidity","b369f8b379d2408d88a545e961cbf6de"]
[null,null,"ｵﾌｨｽ棟","7F","C708会議室","環境センサＡ",null,null,null,"照度","illumination","BF0004E8_illumination","26f342f9c3a24419833c4ff7acd87980","lux"]
[null,null,"ｵﾌｨｽ棟","7F","C708会議室","環境センサＢ","CO2传感器","SZC100","BF0010B9","CO2","CO2","BF0010B9_co2","8eadb1c4a08b49fd9588b63d8b366cb8","ppm"]
[null,null,"ｵﾌｨｽ棟","7F","C708会議室","環境センサＢ",null,null,null,"温度","temperature","BF0010B9_temperature","052f29d8785844a283cf56f1877f9fc2","℃"]
[null,null,"ｵﾌｨｽ棟","7F","C708会議室","環境センサＢ",null,null,null,"湿度","humidity","BF0010B9_humidity","1cf975f67cc64d6cb32a2d625b24a5fb","％"]
[null,null,"ｵﾌｨｽ棟","7F","C708会議室","C708会議室ドア","门磁传感器","DMZ4ZT92","4F00E228","门磁","Gate_magnetism","4F00E228_gate_magnetism","bfd88193d4b64e109210037779fa8951","開／閉"]
[null,null,"ｵﾌｨｽ棟","7F","C708会議室","C708会議室人感","人体感应","IRZ1ZT92","4F00ABB5","人感","Human","4F00ABB5_human","1374fb89c1f0455aa60dd920cd3308df","在／不在"]
[null,null,"ｵﾌｨｽ棟","7F","執務室","ゴミ箱１","JAZE 超声波测距传感器","JZUS91A1","BF001028","超音波距離","Ultrasonic_distance","BF001028_ultrasonic_distance","5d6f688836bb4fb8b66954f5224894f0","cm"]
[null,null,"ｵﾌｨｽ棟","7F","執務室","ゴミ箱２",null,"JZUS91A1","BF001029","超音波距離","Ultrasonic_distance","BF001029_ultrasonic_distance","52a462f51b5f4f7eb2c5ab0d38ddb97d","cm"]
[null,null,"ｵﾌｨｽ棟","7F","執務室","ゴミ箱３",null,"JZUS91A1","BF001032","超音波距離","Ultrasonic_distance","BF001032_ultrasonic_distance","31266c749d3945958297a8f4e090f776","cm"]
[null,null,"実験棟","4F","廊下","照明","光照度传感器","OPZ1ZT92","4F009CC7","照度","illumination","4F009CC7_illumination","2f23943ff4e347f8a66d20461e8ab7ce","lux"]
[null,null,"実験棟","4F","ｻｰﾊﾞｰﾙｰﾑ","環境センサＣ","温湿度传感器","THZ2ZT92","4F00CA48","温度","temperature","4F00CA48_temperature","91d81094ba214191856a9c6f98ab6d0a","℃"]
[null,null,"実験棟","4F","ｻｰﾊﾞｰﾙｰﾑ",{"$nulls":4},"湿度","humidity","4F00CA48_humidity","50395c95b0744efeb68b15734f1693e9","％"]
[null,null,"実験棟","4F","ｻｰﾊﾞｰﾙｰﾑ","接触温度計","ZETA 温度传感器","TZZTZT92","4F00A926","温度(接触)","TZZTZT92","4F00A926_tzztzt92","e6adfc209bcb4b998ba3aca1ba1006ec","℃"]
[null,null,"実験棟","4F","ｻｰﾊﾞｰﾙｰﾑ","接触温度計",null,"TZZTZT92","4F00A928","温度(接触)","TZZTZT92","4F00A928_tzztzt92","75e09fbb590e46de8a7d8925d85649f7","℃"]
[null,null,"実験棟","4F","ｻｰﾊﾞｰﾙｰﾑ","消費電流計","ZETA 電流传感器","CRACZT92","4F00E1D9","電流","Current","4F00E1D9_current","933d9ec462464b0092be281a2d4441b3","A"]
[null,null,"実験棟","4F","実験室２","環境センサＤ","NBI WatcherMini210351830BA390006","NBI-WM0203","BF000BE5","温度","temperature","BF000BE5_temperature","0f6a58638fcf42d2b2f40b6b1c839ba3","℃、％"]
[null,null,"実験棟","4F","実験室２","環境センサＤ",null,null,null,"湿度","humidity","BF0004E8_humidity","cacfec92b38d457e8c4b10b8bf331158"]
[null,null,"実験棟","4F","実験室２","環境センサＤ",null,null,null,"照度","illumination","BF000BE5_illumination","06fa336bf1aa4f7e8e31b333bc5b0053","lux"]
[null,null,"実験棟","4F","実験室２","実験室２人感","人体感应","IRZ1ZT92","4F00AA3D","人感","Human","4F00AA3D_human","acc50f862fc146959b062f86c361a3ce","在／不在"]
[null,null,"実験棟","屋上","屋上緑化","灌水ポンプ","ZETA 4~20ｍA采集器","D4ACZT92","4F00E1B7","超音波流量","Ultrasonic_flow","4F00E1B7_ultrasonic_flow","b10bd923351a4c779a60b23ecde887f6","L/min"]
[null,null,"実験棟","屋上","屋上緑化","土壌","Watcher Pro330491C4143C60012","NBI-WP0403","BF0004F4","土壌温度","Soil_temperature","BF0004F4_soil_temperature","a0351dc40e55459c8711252c7b29bea6","℃、％"]
[null,null,"実験棟","屋上","屋上緑化","土壌",null,null,"BF0004F4","土壌水分量","Soil_water_component","BF0004F4_soil_water_component","2805aa213084428f87dc2d450d531a4c","誘電率"]
[null,null,"実験棟","屋上","屋上緑化","土壌",null,null,"BF0004F4","土壌pH","Soil_pH","BF0004F4_soil_ph","c7bda30200d24f00b239283be16c0d85","pH"]
[null,null,"実験棟","屋上","屋上緑化","土壌",null,null,"BF0004F4","土壌EC","Soil_EC","BF0004F4_soil_ec","7ab7834409d54de1bc1b7a068594478d","dS/m、℃"]
[null,null,"実験棟","屋上","屋上緑化","土壌",null,null,"BF0004F4","葉面温度","Leaf_surface_temperature","BF0004F4_leaf_surface_temperature","253168d7cac042f5a476e6a316763df0","℃"]
[null,null,"実験棟","屋上","屋上緑化","土壌",null,null,"BF0004F4","葉面湿度","Leaf_surface_humidity","BF0004F4_leaf_surface_humidity","c09c1c9e371a4f95b4b6d38ecba997ec","％"]
[null,null,"実験棟","屋上","屋上緑化","土壌",null,null,"BF0004F4","光合成有効放射","Photosynthetic_radiation","BF0004F4_photosynthetic_radiation","f1fa164621cd4e79900a9bc315dd4e02","μmol/m2•s"]
[null,null,"実験棟","屋上","屋上緑化","土壌",null,null,"BF0004F4","気温","temperature","BF0004F4_temperature","63f721aacd8f448c9cc3de5842d67766","℃"]
[null,null,"実験棟","屋上","屋上緑化","土壌",null,null,"BF0004F4","湿度","humidity","BF0004F4_humidity","3d60558aee9c4cf3bd5618c8183a1860","％"]
[null,null,"実験棟","屋上","屋上緑化","土壌",null,null,"BF0004F4","照度","illumination","BF0004F4_illumination","7a18e7d517c042d89f53260ce54e3bc0","lux"]
[null,null,"鉄塔","RF","上部歩廊","傾斜","高精度倾斜传感器","SZT200","BF0010B2","傾斜","Tilt","BF0010B2_tilt","3a4b4a27de5043a9b141c593363c0244","度"]
[null,null,"鉄塔","RF","上部歩廊","気象(RF)","环境传感器","SZW100","BF0010B6","風向","Wind_direction","BF0010B6_wind_direction","81ac8e8f43664f2b857e153e9bd4ac71","0°- 359°"]
[null,null,"鉄塔","RF","上部歩廊","気象(RF)",null,null,null,"風速","Wind_speed","BF0010B6_wind_speed","97a4680c204a4387907f2f24d8d4d02a","m/s"]
[null,null,"鉄塔","RF","上部歩廊","気象(RF)",null,null,null,"瞬間風速","Instantaneous_wind_speed","BF0010B6_Instantaneous_wind_speed","fab142aaee6e4e3e87010baef99e4542","m/s"]
[null,null,"鉄塔","RF","上部歩廊","気象(RF)",null,null,null,"温度","temperature","BF0010B6_temperature","5c613a475bc441aebd02c83554ae38ba","℃"]
[null,null,"鉄塔","RF","上部歩廊","気象(RF)",null,null,null,"湿度","humidity","BF0010B6_humidity","3510451e6dac408f8b3a5f757008cd9f","％"]
[null,null,"鉄塔","RF","上部歩廊","気象(RF)",null,null,null,"照度","illumination","BF0010B6_illumination","dbd320cd6fab4dfbbb53b17d8a19e15d","lux"]
[null,null,"鉄塔","RF","上部歩廊","気象(RF)",null,null,null,"雨量","rainfall","BF0010B6_rainfall","1dbc426b9dae4df7bf0521d70a8ceabc","mm"]
[null,null,"鉄塔","RF","上部歩廊","気象(RF)",null,null,null,"紫外線量","UV_quantity","BF0010B6_uv_quantity","3fd9360463864ffd8da8926b0bf78335","μW/㎠"]
[null,null,"鉄塔","GL","地上部","気象(GL)","环境传感器","SZW100","BF0010B7","風向","Wind_direction","BF0010B7_wind_direction","567dc19a3dca4ade96d9b3b76b894832","0°- 359°"]
[null,null,"鉄塔","GL","地上部","気象(GL)",null,null,null,"風速","Wind_speed","BF0010B7_wind_speed","e85d7528b48e407c94614d4613f624be","m/s"]
[null,null,"鉄塔","GL","地上部","気象(GL)",null,null,null,"瞬間風速","Instantaneous_wind_speed","BF0010B7_Instantaneous_wind_speed","d0fc9e7a4ea64de3ad51919f52e8ead2","m/s"]
[null,null,"鉄塔","GL","地上部","気象(GL)",null,null,null,"温度","temperature","BF0010B7_temperature","90537066959e40d1ac0cca8115e2276f","℃"]
[null,null,"鉄塔","GL","地上部","気象(GL)",null,null,null,"湿度","humidity","BF0010B7_humidity","cc76c11dad5949eab0a4b89139945812","％"]
[null,null,"鉄塔","GL","地上部","気象(GL)",null,null,null,"照度","illumination","BF0010B7_illumination","ed9ea07e484b469dbdd250f67e8092ad","lux"]
[null,null,"鉄塔","GL","地上部","気象(GL)",null,null,null,"雨量","rainfall","BF0010B7_rainfall","3c548bc6692c4b98810b8a16b4bec3c8","mm"]
[null,null,"鉄塔","GL","地上部","気象(GL)",null,null,null,"紫外線量","UV_quantity","BF0010B7_uv_quantity","31a88931f478483898076c9ed7b6bcf7","μW/㎠"]
[null,null,"倉庫","GL","倉庫","環境センサＥ","ZETA 温湿度传感器","THZ2ZT92","4F00CA49","温度","temperature","4F00CA49_temperature","28d259e99539446b93bf216b49d62fac","℃"]
[null,null,"倉庫","GL","倉庫","環境センサＥ",null,null,null,"湿度","humidity","4F00CA49_humidity","99a97c750f074cd0b55d7148876684fa","％"]
[null,null,"ｵﾌｨｽ棟","RF","設備機器置場","高圧受電盤２","ZETA 電流传感器","CRACZT92","4F00E1DB","電流","Current","4F00E1DB_current","97d186eb11194d10b71268145edee650","A"]
[null,null,"実験棟","１Ｆ","消火ポンプ室","消火ポンプ室　ドア","门磁传感器","DMZ4ZT92","4F00E229","门磁","Gate_magnetism","4F00E229_gate_magnetism","b5f6bcbce47349df8fcc4fff980f490c","開／閉"]
[null,null,"実験棟","１Ｆ","消火ポンプ室","泡消火栓　ポンプ１","干接点","OCZ1ZT92","4F007A13","干接点","Dry_contact","4F007A13_dry_contact","7085394cc3824ff8b4972bc3fae5f6b6","運転／停止"]
[null,null,"実験棟","１Ｆ","消火ポンプ室","泡消火栓　ポンプ２","多路干接点","OC16ZT92","4F020A43","運転状態","Driving_condition","4F020A43_driving_condition","ea9070775a174fa1b23040f22f9772cc","運転／停止"]
[null,null,"実験棟","１Ｆ","消火ポンプ室","泡消火栓　ポンプ３",null,null,null,"運転状態","Driving_condition","4F020A43_driving_condition","0b512e4608c9468daab2fe0432d3e61a","運転／停止"]
[null,null,"実験棟","１Ｆ","消火ポンプ室","泡消火栓　ポンプ１","水浸传感器","WDZ1ZT92","4F00A904","漏水(接点)","Leakage","4F00A904_leakage","5efd7956fbaf45b9b7657eeeb0394729","正常／漏水"]
[null,null,"実験棟","１Ｆ","消火ポンプ室","消火栓　ポンプ１","水浸传感器（感应绳）","WDZ3ZT92-1","4F00AAF9","漏水(ｹｰﾌﾞﾙ)","Leakage","4F00AAF9_leakage","d91e816ba89444548786e2005ace442f","正常／漏水"]
[null,null,"実験棟","RF","屋上機器","高圧受電盤２","ZETA 485传感器","D485ZT92","4F00CA19","電圧","Voltage","4F00CA19_voltage","e4c50e08f1c5453ea3c61c5322eed00f","V"]
[null,null,"実験棟","RF","屋上機器","高圧受電盤２",null,null,null,"電流","Current","4F00CA19_current","4efb2c21f224462d929d0b57656394a1","A"]
[null,null,"実験棟","RF","屋上機器","高圧受電盤２",null,null,null,"瞬間電力","Instantaneous_power","4F00CA19_Instantaneous_power","ae9369ac6aca4277bd7af70c61cbcbe6","W"]
[null,null,"実験棟","RF","屋上機器","高圧受電盤２",null,null,null,"積算電量量","Amount_of_charge","4F00CA19_amount_of_charge","4164b3e7c5bf4c268c823bec4a8c795a","A"]

{"sheet":"butics-ax设备","index":2,"n_rows":28,"n_cols":14,"rows_kept":28,"cut":false,"hidden":false,"merged":[[2,1,27,1],[2,2,27,2],[2,3,27,3],[2,4,3,4],[4,4,8,4],[9,4,10,4],[11,4,13,4],[14,4,19,4],[20,4,25,4],[26,4,27,4],[2,5,3,5],[4,5,8,5],[9,5,10,5],[11,5,13,5],[14,5,19,5],[20,5,25,5],[26,5,27,5],[4,6,8,6],[9,6,10,6],[11,6,13,6],[14,6,19,6],[20,6,25,6],[26,6,27,6],[4,7,8,7],[11,7,13,7],[16,7,17,7],[20,7,21,7],[23,7,24,7],[26,7,27,7]]}
[]
[null,"租户","项目","设备号","大楼","楼层","空间","资产","传感器种类","型号","ID","指标","指标 id","单位"]
[null,"NECネッツエスアイ株式会社","KTC","NEC00001","実験棟","１Ｆ","消火ポンプ室","消火栓ポンプ　表示灯(B)","BACnet","BACnet","60e8fd7b-501e-372b-9fc0-e1de27d51d35-AI","表示電圧(B)","d60949df7056428c9cba5cc9b91f04d8","V"]
[{"$nulls":6},"消火ポンプ室","泡消火栓ポンプ　タンク(B)","BACnet","BACnet","7cceca42-fa6d-3783-9968-fb691e5d3cec-AI","圧力(B)","9a322ae64f6b40f0b12d8df0280743ca","Mpa"]
[{"$nulls":4},"ｵﾌｨｽ棟","１Ｆ","エントランス","加圧給水ポンプ(B)","BACnet","BACnet","c4125810-9483-37be-9fe7-8564845fab39-BI","異音(B)","3a96096cb1d048699c6cfc92215047b9","有／無"]
[{"$nulls":8},"BACnet","BACnet","fdfc2ab0-3e32-31c4-8c50-593b405a47bb-BI","異臭(B)","e955a5ecdeda4184a745dbd0c31d097f","有／無"]
[{"$nulls":8},"BACnet","BACnet","223132d1-9b22-36b5-9987-bb88e8d6b7d5-BI","水漏れ","503c404d46084a8dbdbef3e3eaa04d74","有／無"]
[{"$nulls":8},"BACnet","BACnet","8ffca40a-0a99-3ef7-9962-03d8ba12a924-BI","施錠","05dcd00e5f234ebfa245ca67bacecafc","有／無"]
[{"$nulls":8},"BACnet","BACnet","b727daff-7cc1-3fa4-81a3-726bb9e09baa-BI","制御電源表示灯","7065916bd0ba40cca38165cfc9dfb337","点燈／消燈"]
[{"$nulls":4},"ｵﾌｨｽ棟","１Ｆ","EPS","雨水ポンプ　制御盤№１(B)","BACnet","BACnet","6f8aef15-b6cb-32aa-8c94-4cfce134a9cf-AI","電流(B)","e10adef74d7942f6b810f01103d404da","A"]
[{"$nulls":7},"雨水ポンプ　制御盤№２(B)","BACnet","BACnet","379adc2b-f648-3e72-8a58-c77d69e598d5-AI","電流(B)","c3d8e14c236c4c01806671f82bf84acb","A"]
[{"$nulls":4},"ｵﾌｨｽ棟","屋上","設備機器置場","高圧受電盤(B)","BACnet","BACnet","4cda80dc-571b-397c-bb41-094cd43bd7c0-AI","受電電圧(B)","a339e834e8d14a1d9ffa92239be94d02","V"]
[{"$nulls":8},"BACnet","BACnet","df6ed27e-a73c-365f-b13c-361fe6b6664a-AI","電流値(B)","1e9568483d2e46da9d29ca8323981576","A"]
[{"$nulls":8},"BACnet","BACnet","9933766e-3b38-32f5-ba5e-3c531f0cce36-AI","電力(B)","2a1f98b2c2d04a21b26b9d7f13d63e89","W"]
[{"$nulls":4},"ｵﾌｨｽ棟","屋上","設備機器置場","高圧引き込み盤(B)","BACnet","BACnet","94a09f61-5a77-39ca-99a8-6ca64b840cce-ACC","電力量(B)","fa99480a964b49d59a869545e3af407a","KWH"]
[{"$nulls":7},"加湿ポンプ(B)","BACnet","BACnet","d775f29a-69d6-30c7-aebd-d259aabbc217-AI","圧力(B)","99290169143f461d97b2e52e56d6f2c0","Mpa"]
[{"$nulls":7},"循環ポンプ(B)","BACnet","BACnet","7ee9b7b5-6674-3928-ab8d-bec313873d75-AI","1次側圧力(B)","ef7178f7a8b94b59937639cefeb1f251","Mpa"]
[{"$nulls":8},"BACnet","BACnet","84bf8b4c-4418-33ec-a47f-f12f43da8221-AI","2次側圧力(B)","1da95d2ece4849858373299e2658baea","Mpa"]
[{"$nulls":7},"電源装置(ＲＦ)(B)","BACnet","BACnet","d7ffc251-25e1-3e08-8a58-06c948234b32-AI","電源電圧(B)","6aad3e4fbfe14cd38673d89f20e0c5dc","V"]
[{"$nulls":7},"電源装置(６ＲＦ)(B)","BACnet","BACnet","71efcd8f-4848-3a9e-b279-b11dea1dbf0e-AI","電源電圧(B)","e8555bc6005a417aa258bb66afdc75e6","V"]
[{"$nulls":4},"実験棟","屋上","設備機器置場","高圧受電盤(B)","BACnet","BACnet","bc366b7b-8d5c-3892-9b88-806e1e1caf48-AI","受電電圧(B)","655ffc236ce04ab8b2e867ccc1b96dcc","V"]
[{"$nulls":8},"BACnet","BACnet","5883c803-f6d6-3bba-9c04-b2a9e39456b8-AI","電流値(B)","139062cb389448bb810c9b5dc127ba91","A"]
[{"$nulls":7},"高圧引き込み盤(B)","BACnet","BACnet","6276e229-3741-3899-86be-f24b77b1f315-AI","電力量(B)","4580d7bcc9b141b29f3e54ad57fe1006","KWH"]
[{"$nulls":7},"低圧電灯配電盤(B)","BACnet","BACnet","d05f17d7-0370-3cbf-95e6-44f430bf1268-AI","電圧(B)","65d3756d56d74d2d9e34a3de5c88dcd7","V"]
[{"$nulls":8},"BACnet","BACnet","b38bae4d-1af1-3321-95c4-d93659845eb0-AI","電流(B)","cf00ad400f464438a634a3240ee4f1a2","A"]
[{"$nulls":7},"空調機　加湿ポンプ(B)","BACnet","BACnet","9bfc770a-2cb9-3efe-85e5-50bf89cf790a-AI","圧力(B)","3b61caa24a1041bcafd3e9636c5f02bf","Mpa"]
[{"$nulls":4},"実験棟","屋上","植栽散水装置","灌水制御盤(B)","BACnet","BACnet","58417b3c-c99c-3881-b071-308847ed2496-AI","1・2系統電圧(B)","7f6fcf03361a4a2991b18254251961d8","V"]
[{"$nulls":8},"BACnet","BACnet","cc10bec3-b7f8-321b-8335-9a4d6512e7e2-AI","3・4系統電圧(B)","324622d58c0f469c86bdf213825d535c","V"]

{"sheet":"抄表项目","index":3,"n_rows":53,"n_cols":12,"rows_kept":53,"cut":false,"hidden":false,"merged":[[2,1,52,1],[2,2,52,2],[2,3,3,3],[4,3,5,3],[6,3,34,3],[35,3,50,3],[51,3,52,3],[2,4,3,4],[4,4,5,4],[6,4,34,4],[35,4,50,4],[51,4,52,4],[2,5,3,5],[4,5,5,5],[6,5,34,5],[35,5,50,5],[51,5,52,5]]}
[]
[null,"租户","项目","大楼","楼层","空间","表名1","抄表数据",null,"单位","deviceld","指标ID"]
[null,"NECネッツエスアイ株式会社","KTC","実験棟","１Ｆ","消火ポンプ室","消火栓ポンプ　表示灯","表示電圧","消火栓ポンプ　表示灯表示電圧1","V","NEC00003","c6e5af947ed6487292f0ef69018d47e9"]
[{"$nulls":6},"泡消火栓ポンプ　タンク","圧力","泡消火栓ポンプ　タンク圧力2","Mpa","NEC00003","5555a4e5ea714a0c911131bda47943cf"]
[null,null,null,"ｵﾌｨｽ棟","１Ｆ","EPS","雨水ポンプ　制御盤№１","電流","雨水ポンプ　制御盤№１電流3","A","NEC00003","032f7fc3bfaa4c3b94db903ec5d38e91"]
[{"$nulls":6},"雨水ポンプ　制御盤№２","電流","雨水ポンプ　制御盤№２電流4","A","NEC00003","e2f0169ddf9a43b08d5866434d540582"]
[null,null,null,"ｵﾌｨｽ棟","屋上","設備機器置場","高圧受電盤","受電電圧","高圧受電盤受電電圧5","V","NEC00003","80bd04993f3b40ddad887a7f42329090"]
[{"$nulls":7},"電流値","電流値6","A","NEC00003","b904d93723224616a96f7c736a601942"]
[{"$nulls":7},"電力","電力7","W","NEC00003","4e7d6a05b72343fe90413eab4a7c28fa"]
[{"$nulls":6},"高圧引き込み盤","電力量","高圧引き込み盤電力量8","KWH","NEC00003","e581e82ed68b42f2ba82e4e3c4c9c332"]
[{"$nulls":6},"高圧饋電盤","R相","高圧饋電盤R相9","A","NEC00003","d0731874cd054b36b186197d78302948"]
[{"$nulls":7},"S相","S相10","A","NEC00003","3a26aa7fb689490198013a82e80eda37"]
[{"$nulls":7},"T相","T相11","A","NEC00003","9c549848605649d7a4653e2b7f18f1fa"]
[{"$nulls":6},"低圧電灯配電盤No.1","電圧","低圧電灯配電盤No.1電圧12","V","NEC00003","3ac033b6ee7e4b56b086dcd22d5f9e5e"]
[{"$nulls":7},"電流","電流13","A","NEC00003","48f26d07fc0846328e0958a0718acb46"]
[{"$nulls":6},"低圧電灯配電盤No.2","電圧","低圧電灯配電盤No.2電圧14","V","NEC00003","5d016376866c4c3ba6ae9f018ad2c9f9"]
[{"$nulls":7},"電流","電流15","A","NEC00003","eb0f75c470a9424fa2060429fc603226"]
[{"$nulls":6},"低圧動力配電盤No.1","電圧","低圧動力配電盤No.1電圧16","V","NEC00003","62e8eb71740a40f5a07a272f928684e1"]
[{"$nulls":7},"電流","電流17","A","NEC00003","394d7ce3bd3e49c88dadab065ba19054"]
[{"$nulls":6},"低圧動力配電盤No.2","電圧","低圧動力配電盤No.2電圧18","V","NEC00003","3fa9df28f1e846529aed74878806c035"]
[{"$nulls":7},"電流","電流19","A","NEC00003","6dfdd85f2bd24010a459c2b212060302"]
[{"$nulls":6},"電灯変圧器盤No.1","油温","電灯変圧器盤No.1油温20","℃","NEC00003","957e954d55e64394a1634870166e362a"]
[{"$nulls":6},"電灯変圧器盤No.2","油温","電灯変圧器盤No.2油温21","℃","NEC00003","b29766f103e148dcaed3a6b3cf6a4a74"]
[{"$nulls":6},"動力変圧器盤No.1","油温","動力変圧器盤No.1油温22","℃","NEC00003","0ae02bf02c97453fa394503a2b7dbbc4"]
[{"$nulls":6},"動力変圧器盤No.2","油温","動力変圧器盤No.2油温23","℃","NEC00003","dead2f4b30e6472c884ffed5b04dfcb1"]
[{"$nulls":6},"非常動力電灯配電盤","T5 STR 主座 50VA/2 電圧","非常動力電灯配電盤T5 STR 主座 50VA/2 電圧24","V","NEC00003","974cf684edc641ec9858ab65db365a3f"]
[{"$nulls":7},"T5 STR 主座 50VA/2 電流","T5 STR 主座 50VA/2 電流25","A","NEC00003","b178eeba8d994695898e2ce469afccf9"]
[{"$nulls":7},"T5 STR Ｔ座 50VA/2 電圧","T5 STR Ｔ座 50VA/2 電圧26","V","NEC00003","0dbca09de5504899a88c65c47a963c04"]
[{"$nulls":7},"T5 STR Ｔ座 50VA/2 電流","T5 STR Ｔ座 50VA/2 電流27","A","NEC00003","7dd1eaf126c14008aca70c2ab07e4540"]
[{"$nulls":7},"油温","油温28","℃","NEC00003","3d7030a2b5ea4ce6b34219e6da306b35"]
[{"$nulls":6},"加湿ポンプ","圧力","加湿ポンプ圧力29","Mpa","NEC00003","ef3e38b8f8524b949ae79808be790dc7"]
[{"$nulls":6},"循環ポンプ","1次側圧力","循環ポンプ1次側圧力30","Mpa","NEC00003","0ef332e8e7fe4de88f42ead80ae6d198"]
[{"$nulls":7},"2次側圧力","2次側圧力31","Mpa","NEC00003","c94fbfd6bd864baea31526b5e638e94b"]
[{"$nulls":6},"電源装置(ＲＦ)","電源電圧","電源装置(ＲＦ)電源電圧32","V","NEC00003","900941077eea447eb9e0101cb2d2b210"]
[{"$nulls":6},"電源装置(６ＲＦ)","電源電圧","電源装置(６ＲＦ)電源電圧33","V","NEC00003","e576947b113249c5ba208ab6bc56f631"]
[null,null,null,"実験棟","屋上","設備機器置場","高圧受電盤","受電電圧","高圧受電盤受電電圧34","V","NEC00003","669496747edb433e89f76efc499cfa41"]
[{"$nulls":7},"電流値","電流値35","A","NEC00003","8cc21206797e4f1cb1a72f98fcb41ef7"]
[{"$nulls":6},"高圧引き込み盤","電力量","高圧引き込み盤電力量36","KWH","NEC00003","6646d09123aa43dababf604c3e025fea"]
[{"$nulls":6},"低圧電灯配電盤","電圧","低圧電灯配電盤電圧37","V","NEC00003","95e7a979c9ee4ac0a8e5efc4ea0e0176"]
[{"$nulls":7},"電流","電流38","A","NEC00003","2ca7a21cdeba45a491338003ea2c31a1"]
[{"$nulls":6},"低圧動力配電盤No.1","電圧","低圧動力配電盤No.1電圧39","V","NEC00003","e106d17ee0d34d0d99a8aa9a92a4bfa1"]
[{"$nulls":7},"電流","電流40","A","NEC00003","386cf7bd3ee84259942df1fab6d48bbb"]
[{"$nulls":6},"低圧動力配電盤No.2","電圧","低圧動力配電盤No.2電圧41","V","NEC00003","8fda1cfa1b644acba992bf94d9ca61bc"]
[{"$nulls":7},"電流","電流42","A","NEC00003","f99c6fc10ade4e66aad315638189a811"]
[{"$nulls":6},"低圧動力配電盤No.3(420V)","電圧","低圧動力配電盤No.3(420V)電圧43","V","NEC00003","7222c075117746528c9e7951a0bd901f"]
[{"$nulls":7},"電流","電流44","A","NEC00003","e69a9156eb914496b416bd0a7cb6fd8b"]
[{"$nulls":6},"電灯変圧器盤","油温","電灯変圧器盤油温45","℃","NEC00003","285514f505154dd3ad8601e390b80eae"]
[{"$nulls":6},"動力変圧器盤No.1","油温","動力変圧器盤No.1油温46","℃","NEC00003","2589394aeff447dc874483a3ce3c8e6d"]
[{"$nulls":6},"動力変圧器盤No.2","油温","動力変圧器盤No.2油温47","℃","NEC00003","dbea082b112a418fbac579faf72d65be"]
[{"$nulls":6},"動力変圧器盤No.3(420V)","油温","動力変圧器盤No.3(420V)油温48","℃","NEC00003","8df325e2f15a4ad59696d87b8a0e2344"]
[{"$nulls":6},"空調機　加湿ポンプ","圧力","空調機　加湿ポンプ圧力49","Mpa","NEC00003","774a650b7a9b46929eded58cac552ba5"]
[null,null,null,"実験棟","屋上","植栽散水装置","灌水制御盤","1・2系統電圧","灌水制御盤1・2系統電圧50","V","NEC00003","19e96129dff040819df0fdb857a00963"]
[{"$nulls":7},"3・4系統電圧","3・4系統電圧51","V","NEC00003","9af811a00abe4bb4b5c7d1a88873232c"]

{"sheet":"人员定位","index":4,"n_rows":8,"n_cols":14,"rows_kept":8,"cut":false,"hidden":false,"merged":[]}
[]
[null,"租户","项目","大楼","楼层","空间","资产","传感器种类","型号","服务器序列号","ID","指标","指标 id","单位"]
[null,"NECネッツエスアイ株式会社","KTC","ｵﾌｨｽ棟","7F","備品倉庫","台車１",{"$nulls":4},"無:0:ALM　有:1:NMR"]
[{"$nulls":6},"台車２",{"$nulls":4},"無:0:ALM　有:1:NMR"]
[{"$nulls":6},"台車３",{"$nulls":4},"無:0:ALM　有:1:NMR"]
[{"$nulls":6},"脚立１",{"$nulls":4},"無:0:ALM　有:1:NMR"]
[{"$nulls":6},"脚立２",{"$nulls":4},"無:0:ALM　有:1:NMR"]
[{"$nulls":6},"脚立３",{"$nulls":4},"無:0:ALM　有:1:NMR"]

{"sheet":"数据点","index":5,"n_rows":52,"n_cols":9,"rows_kept":52,"cut":false,"hidden":false,"merged":[]}
["租户id(Tenant Id)","组织机构名称(Organization Name)","应用id(App Id)","应用名称(App Name)","设备序列号(Device Id)","设备名称(Device Name)","协议(Protocol)","数据点名称(DataPoint Name)","数据点id(DataPoint Id)"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","雨水ポンプ　制御盤№１電流3","032f7fc3bfaa4c3b94db903ec5d38e91"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","動力変圧器盤No.1油温22","0ae02bf02c97453fa394503a2b7dbbc4"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","T5 STR Ｔ座 50VA/2 電圧26","0dbca09de5504899a88c65c47a963c04"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","循環ポンプ1次側圧力30","0ef332e8e7fe4de88f42ead80ae6d198"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","灌水制御盤1・2系統電圧50","19e96129dff040819df0fdb857a00963"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","動力変圧器盤No.1油温46","2589394aeff447dc874483a3ce3c8e6d"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","電灯変圧器盤油温45","285514f505154dd3ad8601e390b80eae"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","電流38","2ca7a21cdeba45a491338003ea2c31a1"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","電流40","386cf7bd3ee84259942df1fab6d48bbb"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","電流17","394d7ce3bd3e49c88dadab065ba19054"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","S相10","3a26aa7fb689490198013a82e80eda37"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","低圧電灯配電盤No.1電圧12","3ac033b6ee7e4b56b086dcd22d5f9e5e"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","油温28","3d7030a2b5ea4ce6b34219e6da306b35"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","低圧動力配電盤No.2電圧18","3fa9df28f1e846529aed74878806c035"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","電流13","48f26d07fc0846328e0958a0718acb46"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","電力7","4e7d6a05b72343fe90413eab4a7c28fa"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","泡消火栓ポンプ　タンク圧力2","5555a4e5ea714a0c911131bda47943cf"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","低圧電灯配電盤No.2電圧14","5d016376866c4c3ba6ae9f018ad2c9f9"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","低圧動力配電盤No.1電圧16","62e8eb71740a40f5a07a272f928684e1"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","高圧引き込み盤電力量36","6646d09123aa43dababf604c3e025fea"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","高圧受電盤受電電圧34","669496747edb433e89f76efc499cfa41"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","電流19","6dfdd85f2bd24010a459c2b212060302"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","低圧動力配電盤No.3(420V)電圧43","7222c075117746528c9e7951a0bd901f"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","空調機　加湿ポンプ圧力49","774a650b7a9b46929eded58cac552ba5"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","T5 STR Ｔ座 50VA/2 電流27","7dd1eaf126c14008aca70c2ab07e4540"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","高圧受電盤受電電圧5","80bd04993f3b40ddad887a7f42329090"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","電流値35","8cc21206797e4f1cb1a72f98fcb41ef7"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","動力変圧器盤No.3(420V)油温48","8df325e2f15a4ad59696d87b8a0e2344"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","低圧動力配電盤No.2電圧41","8fda1cfa1b644acba992bf94d9ca61bc"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","電源装置(ＲＦ)電源電圧32","900941077eea447eb9e0101cb2d2b210"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","電灯変圧器盤No.1油温20","957e954d55e64394a1634870166e362a"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","低圧電灯配電盤電圧37","95e7a979c9ee4ac0a8e5efc4ea0e0176"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","非常動力電灯配電盤T5 STR 主座 50VA/2 電圧24","974cf684edc641ec9858ab65db365a3f"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","3・4系統電圧51","9af811a00abe4bb4b5c7d1a88873232c"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","T相11","9c549848605649d7a4653e2b7f18f1fa"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","T5 STR 主座 50VA/2 電流25","b178eeba8d994695898e2ce469afccf9"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","電灯変圧器盤No.2油温21","b29766f103e148dcaed3a6b3cf6a4a74"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","電流値6","b904d93723224616a96f7c736a601942"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","消火栓ポンプ　表示灯表示電圧1","c6e5af947ed6487292f0ef69018d47e9"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","2次側圧力31","c94fbfd6bd864baea31526b5e638e94b"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","高圧饋電盤R相9","d0731874cd054b36b186197d78302948"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","動力変圧器盤No.2油温47","dbea082b112a418fbac579faf72d65be"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","動力変圧器盤No.2油温23","dead2f4b30e6472c884ffed5b04dfcb1"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","低圧動力配電盤No.1電圧39","e106d17ee0d34d0d99a8aa9a92a4bfa1"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","雨水ポンプ　制御盤№２電流4","e2f0169ddf9a43b08d5866434d540582"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","電源装置(６ＲＦ)電源電圧33","e576947b113249c5ba208ab6bc56f631"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","高圧引き込み盤電力量8","e581e82ed68b42f2ba82e4e3c4c9c332"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","電流44","e69a9156eb914496b416bd0a7cb6fd8b"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","電流15","eb0f75c470a9424fa2060429fc603226"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","加湿ポンプ圧力29","ef3e38b8f8524b949ae79808be790dc7"]
["f8aac6a9046244bb97c9d6144f70430a","介谷科技","4ebe6a582ca24082896c7a4da8efd9d3","sentry-NECネッツエスアイ株式会社","NEC00003","NEC抄表","godzilla-json","電流42","f99c6fc10ade4e66aad315638189a811"]

{"sheet":"Sheet1","index":6,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}